# Draft Report on grid event Complete outage of 220kV Sabarigiri PH of KSEB in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 15-06-2026 15:30

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was failure of the R-phase pole of the Generator Main Circuit Breaker of Unit-5 to open during a normal shutdown of the generating unit leading to operation of the Local Breaker Backup (LBB) protection and further due to an isolator discrepancy associated with Unit-5, both the 220 kV Main Bus and 220 kV Transfer Bus were tripped leading to the Complete outage of 220kV Sabarigiri PH of KSEB.

- Time and Date of the Event (घटना का समय और दिनांक:  02-06-2026 06:37

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU , KERALA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 16800 | 16812 |
| TamilNadu State Generation (MW) | 5429 | 5467 |
| Kerala State Demand (MW) | 3837 | 3846 |
| Kerala State Generation (MW) | 692 | 612 |
| Grid Frequency (Hz) | 50.04 | 50.04 |
| SR Demand (MW) | 52416 | 52572 |
| SR Generation (MW) | 43940 | 43945 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

Connectivity at 220kV Sabarigiri PH

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 168.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 8 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-EDAMON-SABARIGIRI-3

      - 220KV-EDAMON-SABARIGIRI-1

      - 220KV-EDAMON-SABARIGIRI-2

      - 220KV-SABARIGIRI-PALLOM-1

      - 220KV-THENI-SABARIGIRI-1

      - 220KV-AMBALAMUGAL-SABARIGIRI-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

At the time of the incident, Unit-5, Unit-6, 220KV-SABARIGIRI-PATHANAMTHITTA-1, 220KV-SABARIGIRI-PALLOM-1 , 220KV-EDAMON-SABARIGIRI-2 , 220KV-EDAMON-SABARIGIRI-3 and the 50 MVA Transformer were connected to the 220 kV Main Bus, while Unit-1, Unit-3, Unit-4, 220KV-THENI-SABARIGIRI-1 and 220KV-AMBALAMUGAL-SABARIGIRI-1 were connected to the 220 kV Transfer Bus.

During taking out of Unit-5, where in commands were issued to stop the turbine governor, open the Field Breaker, and open the Generator Main Circuit Breaker (GCB). While the Field Breaker opened successfully and the governor stop command was executed, the R-phase pole of the Generator Main Circuit Breaker failed to open due to a mechanical defect (as per FIR) where in after few seconds Minimum Impedance Protection and Voltage Controlled Overcurrent Protection operated and since the breaker failed to open led to the operation of LBB (As per PMU, around 6 secs of voltage dip was observed). However, due to an existing isolator discrepancy associated with Unit-5, the Busbar Protection scheme identified Unit-5 as being connected to both the 220 kV Main Bus and the 220 kV Transfer Bus and hence both bus sections and tripped all associated bays and DT was sent to remote ends (for lines). This led to the Complete outage of 220kV Sabarigiri PH of KSEB.

- DR Analysis:

220KV-THENI-SABARIGIRI-1

|  | THENI - 220KV | SABARIGIRI - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:02-06-2026 06:37:51.245 DT RECIEVE ARR L/O, 3PH INI TO B/B Ir (max): 0.04 kA Iy (max): 0.04 kA Ib (max): 0.05 kA Vr (max): 138.27 kV Vy (max): 159.12 kV Vb (max): 141.85 kV | No DR uploaded |

SABARIGIRI - 220KV

|  | SABARIGIRI - 220KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:07-05-2026 18:22:44.490 [VO.25] I> Alarm Ir (max): 3.04 kA Iy (max): 0.28 kA Ib (max): 0.19 kA DR Trigger Time:02-06-2026 07:01:58.775 [VO.25] I> Alarm [BO.03] TRIP COIL 1, [BO.04] TRIP COIL 2, [VO.26] CBF St1 Trip Ir (max): 0.74 kA Iy (max): 0.00 kA Ib (max): 0.00 kA DR Trigger Time:02-06-2026 07:02:00.305 [VO.15] BB CBF Trip Ir (max): 0.45 kA Iy (max): 0.00 kA Ib (max): 0.00 kA |

- A) PMU Analysis:

From PMU data, R-ph voltage dip can be observed from 06:37:45.360 to 06:37:51.240 Hrs.

B) SCADA Analysis:

From SCADA tripping of Unit-1, Unit-3, Unit-4, Unit-5, Unit-6 220kV can be observed at 06:38hrs on the same day

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| KSEB | 1. Non opening of R phase pole of generator circuit breaker needs review 2. Non operation of LBB after hand tripping of the Unit-5 needs review 3. Tripping of both the buses due to isolator discrepancy associated with Unit-5 needs review. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| KSEB | 1. Following the busbar protection operation and subsequent outage, restoration activities were carried out at Sabarigiri Power Station. Units-1, Units-3, Units-4, and Units-6 were kept under Restricted Shutdown (RSD). The 220 kV Sabarigiri–Pathanamthitta feeder could not be restored along with the other feeders. The feeder was charged from the Pathanamthitta end at 08:22 Hrs; however, while attempting to tie the feeder at the Sabarigiri end, it tripped at 08:25 Hrs on Pole Discrepancy Protection indication. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

Following the busbar protection operation and subsequent outage, restoration activities were carried out at Sabarigiri Power Station.

Units-1, Units-3, Units-4, and Units-6 were kept under Restricted Shutdown (RSD). The transmission feeders were restored in a phased manner as detailed below:

220 kV Sabarigiri–Edamon #2 feeder charged at 07:45 Hrs

220 kV Sabarigiri–Edamon #3 feeder charged at 07:46 Hrs

220 kV Sabarigiri–Ambalamugal feeder charged at 08:15 Hrs

220 kV Sabarigiri–Theni feeder charged at 08:16 Hrs

220 kV Sabarigiri–Pallom feeder charged at 08:27 Hrs

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) |  |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 |  |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 | KSEB |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: