# Draft Report on grid event Tripping of 220kV Bus-1 of 220kV VTPS Generating Station of APGENCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 11-06-2026 14:08

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was Y-B fault in 220kV VTPS Rentachinthala Line-1. At VTPS end, B-pole did not open causing 220kV Bus-1 LBB to operate. Immediately, 220kV VTPS Bus-1 LBB operated and all elements connected to the Bus-1 tripped. This led to the Tripping of 220kV Bus-1 at 220kV VTPS Generating Station of APGENCO

- Time and Date of the Event (घटना का समय और दिनांक:  25-05-2026 17:08

- Event Category (ग्रिड घटना का प्रकार):  GI-1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): ANDHRA PRADESH

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Andhra Pradesh State Demand (MW) | 11846 | 11765 |
| Andhra Pradesh State Generation (MW) | 8598 | 8137 |
| Grid Frequency (Hz) | 49.98 | 49.97 |
| SR Demand (MW) | 56652 | 56578 |
| SR Generation (MW) | 53123 | 53000 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 220KV-VTPS-RENTACHINTHALA-2 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Thunders |

Bus configuration at VTPS:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 457.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 28 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-VTPS-PIDUGURALLA-1

      - 220KV-TADIKONDA-VTPS-1

      - 220KV-VTPS-CHILLAKALLU-1

      - 220KV-GUNADALA-VTPS-1

      - 220KV-KONDAPALLI-VTPS-1

      - 220KV-VTPS-PODILI-1

      - 220KV-VTPS-RENTACHINTHALA-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

220kV VTPS Rentachinthala Line-1 is connected to Bus-1 at VTPS. As per the reports submitted, the triggering incident was Y-B fault in 220kV VTPS Rentachinthala Line-1. At Rentachinthala end, the fault was sensed in Z1 and 3ph tripped. At VTPS end, the fault was sensed in Z1, and where in Y and R poles got opened, but B-pole current was still conducting and LBB operated after around 200ms and all elements connected to the Bus-1 tripped ( 220KV-VTPS-PIDUGURALLA-1, 220KV-TADIKONDA-VTPS-1, 220KV-VTPS-CHILLAKALLU-1, 220KV-GUNADALA-VTPS-1, 220KV-KONDAPALLI-VTPS-1, 220KV-VTPS-PODILI-1, 220KV-VTPS-RENTACHINTHALA-1, VTPS-U1, VTPS-U4, VTPS-U5). This led to the Tripping of 220kV Bus-1 at 220kV VTPS Generating Station of APGENCO and due to the tripping of U1, U4 and U5 led to a generation loss of around 457MW.

- DR Analysis:

VTPS - 220KV

|  | VTPS - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Bus Outage |

220KV-VTPS-RENTACHINTHALA-1

|  | VTPS - 220KV | RENTACHINTHALA - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:25-05-2026 17:08:30.150 Any Trip, DIST Trip A, DIST Trip B, DIST Trip C, Z1, M_CB R PH TRIP, M_CB Y PH TRIP, M_CB B PH TRIP, T_BC R PH TRIP, T_BC Y PH TRIP, T_BC B PH TRIP, CARR SEND, TRIP 86 B, ANNUNCIATION, TRIP 86 R, TRIP 86 Y, TRIP 86 B CARR RECEIVED CB OPEN BB OPTD, BB OPTD Ir (max): 0.09 kA Iy (max): 3.15 kA Ib (max): 2.93 kA Vr (max): 131.07 kV Vy (max): 131.47 kV Vb (max): 131.26 kV DR Trigger Time:25-05-2026 17:08:30.140 OSC Trigger On, POWER SWING 50DD PH DIST Z4 PKP PH DIST Z2 PKP, PH DIST Z3 PKP PH DIST Z2 PKP, PH DIST Z3 PKP, PH DIST Z4 PKP ZONE 1 TRIP On, PUTT TX1, PH DIST Z1 PKP PUTT OP, CARR RCVD On CB R-PH STAT Off, CB B-PH STAT Off BKR OPEN On, CB Y-PH STAT Off, GND DIST Z2 PKP, GND DIST Z3 PKP OSC Trigger On, BB/LBB/RE_TR On POWER SWING 50DD Ir (max): 0.09 kA Iy (max): 2.99 kA Ib (max): 2.91 kA Vr (max): 150.39 kV Vy (max): 128.69 kV Vb (max): 128.05 kV | DR Trigger Time:25-05-2026 17:08:30.149 DIST Fwd DIST Trip A, DIST Trip B, DIST Trip C, DIST Sig. Send, Z1, AR Lockout Shot>, BAR, ZONE-1 R PH TRIP, ZONE-1 Y PH TRIP, ZONE-1 B PH TRIP, 86A OPTD, 86B OPTD 86A&B+96 OP DIST UNB CR MCB B PH OPEN MCB R PH OPEN, MCB Y PH OPEN Ir (max): 0.05 kA Iy (max): 7.19 kA Ib (max): 6.91 kA Vr (max): 138.92 kV Vy (max): 135.19 kV Vb (max): 133.75 kV |

- A) PMU Analysis:

From PMU, dip in Y-B fault is observed indicating Y-B fault during the event with delayed fault clearance.

B) SCADA Analysis:

From SCADA tripping of VTPS Bus-1 can be observed with generation tripping during the event.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| APGENCO | 1. Non opening/current conduction of the breaker leading to LBB operation needs review 2. Non-availability of Re-Trip needs review 3. Non-sending of DT to remote ends for LBB operation needs review |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| APGENCO | 1. The B phase Chamber of Rentachintala-1 CB has to be inspected |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

25/05/2026 17:36

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | APGENCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | APTRANSCO |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | APGENCO |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: