# Draft Report on grid event Tripping of 400kV and 220kV Bus-1 at Gajwel of TGTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 15-06-2026 19:05

# Event Summary (घटना का सारांश):

# During the antecedent condition, 400KV-GAJWEL-NARSAPUR-2, 400KV-RAMADUGU-GAJWEL-1 and 400KV-RAMADUGU-GAJWEL-2 was under outage. As per the reports submitted, the triggering incident is 220kV Bus-1 B-ph Bus PT failure leading to the operation of 220kV BBP and tripping of all elements connected to 220kV Bus-1 at Gajwel. During the same time, 400kV Bus-1 also tripped due to LBB maloperation. This led to the Tripping of 400kV and 220kV Bus-1 at Gajwel of TGTRANSCO.

- Time and Date of the Event (घटना का समय और दिनांक:  27-05-2026 06:02

- Event Category (ग्रिड घटना का प्रकार):  GI-2

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TELANGANA

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Telangana State Demand (MW) | 7551 | 7535 |
| Telangana State Generation (MW) | 5123 | 5143 |
| Grid Frequency (Hz) | 50.09 | 50.08 |
| SR Demand (MW) | 45755 | 45542 |
| SR Generation (MW) | 46727 | 46515 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 400KV-RAMADUGU-GAJWEL-1 - 400KV-RAMADUGU-GAJWEL-2 - 400KV-GAJWEL-NARSAPUR-2 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Rainy , Thunders , Windy |

Bus Configuration of 400 kV side at Gajwel 400/220/132kV SS :

Bus Configuration of 220 kV side at Gajwel 400/220/132kV SS :

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 43 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 400KV/220KV GAJWEL-ICT-1

      - 400KV/220KV GAJWEL-ICT-2

      - 400KV-GAJWEL-RAMAGUNDAM-1

      - 400KV-GHANAPUR-GAJWEL-1

      - GAJWEL - 400KV - Bus 1

      - GAJWEL - 220KV - Bus 1

      - 400KV-GAJWEL-CHANDALAPUR-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

During the antecedent condition, 400KV-GAJWEL-NARSAPUR-2 was under outage from 26-05-2026 21:40 Hrs, 400KV-RAMADUGU-GAJWEL-1 was under outage from 26-05-2026 21:40 Hrs and 400KV-RAMADUGU-GAJWEL-2 was under outage from 26-05-2026 21:54 Hrs. Since 400KV-GAJWEL-NARSAPUR-2 was under out condition, 400KV-GAJWEL-CHANDALAPUR-1 was only connected to 400kV Bus-1.

As per reports submitted, on 27-05-2026 at 06:02hrs, 220kV B-phase Bus-1 PT blasted causing 220kV Bus-1 busbar protection operation and tripped all the elements connected to 220kV Bus-1 at 400/220/132kV SS Gajwel. 315MVA ICT-1 & 500MVA ICT-2 HV breakers (Main & Tie) tripped on inter trip. With the tripping of the ICT-1 and 2 HV side breakers (main and tie) and hence 400KV-GAJWEL-RAMAGUNDAM-1 and 400KV-GHANAPUR-GAJWEL-1 were only connected to 400kV Bus-1. During the event, Bus Reactor Tie breaker (directly connected to bus-1 because of half dia) PU relay initiated backtrip command to CU without any external LBB relay initiation and immediately led to the tripping of all main breakers connected to 400kV Bus-1 but the BR breaker(415) did not trip and was holding. This led to the Tripping of 400kV and 220kV Bus-1 at Gajwel of TGTRANSCO and further as 400KV-GAJWEL-CHANDALAPUR-1, 400KV-GAJWEL-RAMAGUNDAM-1 and 400KV-GHANAPUR-GAJWEL-1 were only connected to 400kV Bus-1 and tripping of 400kV Bus-1 led to the tripping of 400KV-GAJWEL-CHANDALAPUR-1, 400KV-GAJWEL-RAMAGUNDAM-1 and 400KV-GHANAPUR-GAJWEL-1. However, DT was not sent to 400KV-GAJWEL-CHANDALAPUR-1, 400KV-GAJWEL-RAMAGUNDAM-1 and 400KV-GHANAPUR-GAJWEL-1.

- DR Analysis:

400KV/220KV GAJWEL-ICT-1

|  | GAJWEL - 400KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:27-05-2026 06:03:19.823 Device FltDet, Device Trip, BB Trip L123 Ir (max): 4.70 kA Iy (max): 4.70 kA Ib (max): 4.70 kA |

400KV/220KV GAJWEL-ICT-2

|  | GAJWEL - 400KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:27-05-2026 06:03:19.826 Device FltDet, Device Trip, BB Trip L123 Ir (max): 9.99 kA Iy (max): 9.99 kA Ib (max): 9.99 kA |

400KV-GAJWEL-RAMAGUNDAM-1

|  | GAJWEL - 400KV | RAMAGUNDAM - 400KV |
| --- | --- | --- |
| Time Sync Issue | Yes | No |
| DR Analysis | DR Trigger Time:27-05-2026 06:01:04.912 Any Trip, Internal Trip, Relay Label 01, Relay Label 02, Relay Label 03, Trip 50BF (CU) Ir (max): 0.29 kA Iy (max): 0.11 kA Ib (max): 0.41 kA | DR Trigger Time:27-05-2026 06:02:59.588 PHS-STPE PHS-STFWL3 DEF_START PHS-STFW1PH PHS-STPP Ir (max): 0.30 kA Iy (max): 0.57 kA Ib (max): 1.50 kA Vr (max): 240.15 kV Vy (max): 241.06 kV Vb (max): 239.24 kV |

400KV-GHANAPUR-GAJWEL-1

|  | GHANAPUR - 400KV | GAJWEL - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | Yes |
| DR Analysis | DR not triggered. | DR Trigger Time:27-05-2026 06:01:04.911 Any Trip, Internal Trip, Relay Label 01, Relay Label 02, Relay Label 03, Trip 50BF (CU) Ir (max): 0.31 kA Iy (max): 0.57 kA Ib (max): 1.18 kA |

GAJWEL - 400KV

|  | GAJWEL - 400KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:27-05-2026 06:01:04.903 Ext. 3 ph Trip Any Trip, Breaker Failure, CBF Ext Backtrip Any Trip, Internal Trip, Relay Label 01, Relay Label 02, Relay Label 03, Trip 50BF (CU) Ir (max): 0.25 kA Iy (max): 0.26 kA Ib (max): 0.92 kA DR Trigger Time:27-05-2026 06:01:04.911 Trip 50BF Zone 1, Trip 50BF Ir (max): 0.10 kA Iy (max): 0.10 kA Ib (max): 0.11 kA |

GAJWEL - 220KV

|  | GAJWEL - 220KV |
| --- | --- |
| Time Sync Issue | Yes |
| DR Analysis | DR Trigger Time:27-05-2026 06:03:19.613 Trip BBP G_MCU 7SS522 V4.7, Trip BUS1 G_MCU 7SS522 V4.7, Device FltDet_1_897B_7SS525 V3.3, Device Trip_1_897B_7SS525 V3.3, BB Trip L123_1_897B_7SS525 V3.3 Device FltDet_3_897B_7SS525 V3.3, Device FltDet_7_897B_7SS525 V3.3, Device Trip_7_897B_7SS525 V3.3, BB Trip L123_7_897B_7SS525 V3.3, Device FltDet_9_897B_7SS525 V3.3, Device Trip_9_897B_7SS525 V3.3, BB Trip L123_9_897B_7SS525 V3.3, Device FltDet_10_897B_7SS525 V3.3, Device Trip_10_897B_7SS525 V3.3, BB Trip L123_10_897B_7SS525 V3.3, Device FltDet_14_897B_7SS525 V3.3, Device Trip_14_897B_7SS525 V3.3, BB Trip L123_14_897B_7SS525 V3.3, Device FltDet_16_897B_7SS525 V3.3, Device FltDet_19_897B_7SS525 V3.3, Device Trip_19_897B_7SS525 V3.3, BB Trip L123_19_897B_7SS525 V3.3, Device FltDet_23_897B1_7SS525 V3.3 Device Trip_3_897B_7SS525 V3.3, BB Trip L123_3_897B_7SS525 V3.3, Device Trip_16_897B_7SS525 V3.3, BB Trip L123_16_897B_7SS525 V3.3, Device Trip_23_897B1_7SS525 V3.3, BB Trip L123_23_897B1_7SS525 V3.3 Device FltDet_6_897B_7SS525 V3.3, Device Trip_6_897B_7SS525 V3.3, BB Trip L123_6_897B_7SS525 V3.3 Ir (max): 0.55 kA Iy (max): 0.55 kA Ib (max): 0.55 kA |

- A) PMU Analysis:

From the PMU plot, tripping of 400KV-GHANAPUR-GAJWEL-1 and 400KV-GAJWEL-RAMAGUNDAM-1 line at Gajwel end can be observed with line holding at remote ends.

B) SCADA Analysis:

From SCADA plot, tripping of 400 kV BUS-1 and 220 kV BUS-1 of Gajwel 400/220/132kV SS can be observed.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TGTRANSCO | 1. Unwanted operation of LBB by bus reactor tie breaker PU relay and tripping of 400kV Bus-1 needs review 2. Non opening of 415 BR breaker for LBB operation needs review 3. Non sending of DT to remote ends during non availability of tie breaker and LBB operation (400kV Bus-1) |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| TGTRANSCO | - Replaced the damaged 220KV Bus-1 PT and charged the Bus. Replaced the suspected cable of reactor tie bay LBB relay to tie PU on 05-06-2026 Rectified the CU & PU DRs GPS time sync issue on 27-05-2026. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TGTRANSCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | TGTRANSCO, NTPC_RSTPS |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | TGTRANSCO |
| 4 | Any other non-compliance | IEGC section 17.3 | TGTRANSCO |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: