# Draft Report on grid event Tripping of 400kV Bus-2 of 400kV Alamathy SS of TANTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 19-06-2026 20:54

# Event Summary (घटना का सारांश):

# As per the reports submitted, the triggering incident was R-G fault in 400kV Alamathy-Manali line due to failure of R phase supporting insulator whihc eventually caused R-G fault in 400kV Bus-2. Immediately, 400kV Bus-2 BBP operated and all main breakers connected to 400kV Bus-2 tripped. This led to loss of power supply to 400kV Alamathy Bus-2.

- Time and Date of the Event (घटना का समय और दिनांक:  03-06-2026 18:00

- Event Category (ग्रिड घटना का प्रकार):  GD - 1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TAMILNADU

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| TamilNadu State Demand (MW) | 18091 | 17227 |
| TamilNadu State Generation (MW) | 8187 | 7473 |
| Grid Frequency (Hz) | 50.09 | 50.2 |
| SR Demand (MW) | 52816 | 51499 |
| SR Generation (MW) | 48118 | 46880 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Rainy |

At 400kV Alamathy SS:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 6 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 400KV/230KV ALAMATHY-ICT-4

      - 400KV/110KV ALAMATHY-ICT-1

      - 400KV-VALLUR-ALAMATHY-2

      - 400KV-ALAMATHY-MANALI-1

      - 400KV-ALAMATHY-NCTPS_STAGE_II-1

      - 400KV-VALLUR-ALAMATHY-2

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

At 18:00hrs:

Due to heavy wind and rain, At 400kV Alamathy SS at 18.00 hrs, the triggering incident was R-G fault in 400kV Alamathy-Manali line due to failure of R phase supporting insulator . At both ends, the fault was sensed in zone-1. At Alamathy end, A/R operated and the line tripped on persistent fault. During the second fault after A/R dead time the fault developed into R-G fault in 400kV Alamathy 400kV Bus-2. Immediately, 400kV Bus-2 BBP operated and all main breakers connected to 400kV Bus-2 tripped. This led to loss of power supply to 400kV Alamathy Bus-2. At Manali end, the fault was sensed in zone-1. After A/R dead time A/R did not operate and the line tripped.

At 18:03hrs:

At 18:03hrs, during rain Y-G fault was observed in 400kV Alamathy NCTPS_STAGE_II-1. At both ends, the fault was sensed in zone-1 and Y-pole opened. However, though A/R close signal is seen, A/R did not operate at both ends and line tripped on PD.

At 18:30hrs:

During the Bus-2 BBP operation, the 400 kV Alamathy Vallur-2 main CB tripped and the feeder was subsequently charged through the tie CB, as the 400 kV Alamathy Vallur-1 line was in service through Bus-1 and both lines are in the same dia.

It was reported that a heavy arc was observed at the Bus-1 side isolator of the 400 kV Alamathy Vallur-1 line. Consequently, the main CB of the 400 kV Alamathy Vallur-1 line was manually tripped at 18:30 hrs, resulting in the tripping of both 400kV Alamathy Vallur-1 &2.

SPS operation:

At Manali, Manali SPS has operated and a load relief of around 226MW was observed as the flow on 400kV Manali NCTPS was going around 740MW immedeately after tripping of 400 kV Alamathy-Manali

- DR Analysis:

400KV-ALAMATHY-MANALI-1

|  | ALAMATHY - 400KV | MANALI - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis |  |  |

400KV-ALAMATHY-NCTPS_STAGE_II-1

|  | ALAMATHY - 400KV | NCTPS_STAGE_II - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:03-06-2026 18:03:15.529 POWER SWING OUTER GND DIST Z3 PKP, DEF BLK On TRIPBUS 5 OP, TRIP PHASE B, GND DIST Z1 OP, GND DIST Z2 PKP, PUTT TX1, POWER SWING INNER, TRIP 1-POLE AR RIP PUTT RECD On AR FORCE 3P TRIP 1252 B CLOSE Off AR 1-P RIP 1252 B CLOSE On 1252 B CLOSE Off AR CLOSE BKR1 AR LO TRIPBUS 5 OP 1252 A CLOSE Off, 1252 C CLOSE Off Ir (max): 1.01 kA Iy (max): 31.01 kA Ib (max): 2.37 kA Vr (max): 249.85 kV Vy (max): 233.52 kV Vb (max): 250.04 kV | DR Trigger Time:03-06-2026 18:03:15.518 Any Start I>4 Start DIST Fwd Any Trip, DIST Trip B, Z1 L10_CAR RECV CH2 L2_MCB B-PH OPEN Ir (max): 1.02 kA Iy (max): 8.94 kA Ib (max): 2.41 kA Vr (max): 233.74 kV Vy (max): 233.73 kV Vb (max): 234.61 kV DR Trigger Time:03-06-2026 18:03:15.521 Started Phase B I>4 Start Zone 1 B Trip, Zone 1 N Trip, Any Trip L13 CAR RECV CH1 Aid 1 Dist Trip L2 MCB Bph OPEN Started Phase C, I>4 Start Ir (max): 1.01 kA Iy (max): 8.93 kA Ib (max): 2.41 kA Vr (max): 233.94 kV Vy (max): 233.86 kV Vb (max): 234.70 kV |

400KV-VALLUR-ALAMATHY-2

|  | ALAMATHY - 400KV | VALLUR - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Loss of busbar | Loss of busbar |

400KV/230KV ALAMATHY-ICT-4

|  | ALAMATHY - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:03-06-2026 18:00:11.997 DI3 HV MCB OPEN Ir (max): 2.02 kA Iy (max): 0.31 kA Ib (max): 0.54 kA |

400KV-VALLUR-ALAMATHY-1

|  | ALAMATHY - 400KV | VALLUR - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | Hand tripped at Alamathy end | Hand tripped at Alamathy end |

ALAMATHY - 400KV

|  | ALAMATHY - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | Loss of busbar |

- A) PMU Analysis:

From the PMU plot, R-G fault can be observed without any delayed fault clearance

B) SCADA Analysis:

From SCADA data, Alamathy Bus 2 tripping is observed at 18:00 during the event

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| TANTRANSCO | 1. Non operation of A/R at Manali end in 400kV Alamathi Manali line. 2. Non operatin of A/R on Alamathy end in 400KV-ALAMATHY-NCTPS_STAGE_II-1. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| TANTRANSCO | 1. Test charged tood OK |
| NTECL | 1. Hand tripped at Alamathy end |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

The 315 MVA, 400/230 kV ICT-4 was restored at 20:49 hrs on 03.06.2026. Subsequently, the 400 kV Alamathy–Manali Line was restored at 02:41 hrs on 04.06.2026. The 400 kV Alamathy–Sunguvarchatram-2 Line was restored at 13:20 hrs on 04.06.2026.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | TANTRANSCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 | NTECL, TANTRANSCO |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) | TANTRANSCO |
| 4 | Any other non-compliance | IEGC section 17.3 | TNPGCL, TANTRANSCO |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: