# Draft Report on grid event Tripping of 400kV Kalpakka Bus-3 of APTRANSCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 15-06-2026 16:33

# Event Summary (घटना का सारांश):

# The triggering incident is the 4" IPS pipe connector failure in 400 kV Bay-424 (PGCIL-2 Bay) and came into contact with R-phase, resulting in R-G Bus fault in Bus-3. Subsequently, Bus-3 Busbar Protection operated and tripped all Bus-3 connected elements, namely 400kV Simhadri–Kalpakka-2, 400kV Kalpakka–Vemagiri AP-1, 400kV Gazuwaka–Kalpakka-2 and 400/220kV ICT-3 and Direct Transfer Trip signals were also transmitted to the corresponding remote substations. This led to the Tripping of 400kV Kalpakka Bus-3 of APTRANSCO

- Time and Date of the Event (घटना का समय और दिनांक:  09-06-2026 19:26

- Event Category (ग्रिड घटना का प्रकार):  GI-2

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): ANDHRA PRADESH

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Andhra Pradesh State Demand (MW) | 10371 | 10218 |
| Andhra Pradesh State Generation (MW) | 8163 | 8175 |
| Grid Frequency (Hz) | 50.08 | 50.08 |
| SR Demand (MW) | 53984 | 53821 |
| SR Generation (MW) | 52107 | 51980 |

*Pre and post data of 1 minute before and after the event

| Elements under outage | - 400KV-KALPAKKA-ASUPAKA-1 - 400KV-KALPAKKA-KHAMMAM_PG-2 |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 0.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  1 hours, 56 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण): 
       NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 400KV-SIMHADRI-KALPAKKA-2

      - 400KV-KALPAKKA-VEMAGIRI_AP-1

      - 400KV-GAZUWAKA-KALPAKKA-2

      - 400KV/220KV KALPAKKA-ICT-3

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

The triggering incident is the 4" IPS pipe connector located in the R-phase section between the Line Isolator and TBC Isolator failure and became disconnected from its support in 400 kV Bay-424 and came in contact with R-phase equipment creating a R-G Bus fault within the Bus-3 protection zone as shown below.

Hence, Bus-3 BBP Protection operated and tripped all Bus-3 connected elements, namely 400 kV Simhadri–Kalpakka-2, 400 kV Kalpakka–Vemagiri AP-1, 400 kV Gazuwaka–Kalpakka-2 and 400/220 kV Kalpakka ICT-3 and DT was sent to remote ends (for lines) and remote ends tripped. This led to the Tripping of 400kV Kalpakka Bus-3 of APTRANSCO.

- DR Analysis:

400KV-SIMHADRI-KALPAKKA-2

|  | SIMHADRI - 400KV | KALPAKKA - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:09-06-2026 19:26:27.681 IOC ALARM ZONE-3 START any start DEF START ZONE-2 START CARRIER SEND DT RCVD CH1 GENERAL TRIP, 3ph trip, TRIP_RPH, TRIP_YPH, TRIP_BPH, AR BLOCK mcb, TCB AR INHBI, MCB AR INHIBI DT RECI CH2 86A OPTD, 86A OPTD 86B OPTD PR3P MCB AR, PRE3PH TCB AR AR INHB FB M1 Ir (max): 7.24 kA Iy (max): 1.61 kA Ib (max): 0.50 kA Vr (max): 236.30 kV Vy (max): 238.70 kV Vb (max): 256.01 kV DR Trigger Time:09-06-2026 19:26:27.735 IOC ALARM ZONE-3 START any start DEF START ZONE-2 START CARRIER SEND DT RCVD CH1 GENERAL TRIP, 3ph trip, TRIP_RPH, TRIP_YPH, TRIP_BPH, AR BLOCK mcb, TCB AR INHBI, MCB AR INHIBI DT RECI CH2 86A OPTD, 86A OPTD 86B OPTD PR3P MCB AR, PRE3PH TCB AR AR INHB FB M1 Ir (max): 7.24 kA Iy (max): 1.61 kA Ib (max): 0.50 kA Vr (max): 236.30 kV Vy (max): 238.71 kV Vb (max): 256.01 kV | DR Trigger Time:09-06-2026 19:26:27.681 Trip L1 CZ Device trip G, Trip L1 G, Trip BBP G, Trip BUS3 G |

400KV-KALPAKKA-VEMAGIRI_AP-1

|  | KALPAKKA - 400KV | VEMAGIRI_AP - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:09-06-2026 19:26:27.681 Trip L1 CZ Device trip G, Trip L1 G, Trip BBP G, Trip BUS3 G | DR Trigger Time:09-06-2026 19:26:27.743 DIST ND ST L1 STARTZ3, STARTZ4 DT RECV CH1 DT RECVD 3PH GR-A OPTD 3PH GR-B OPTD DT RECV CH2 LBB INITIATIO AR BLOCK(DR) Ir (max): 1.90 kA Iy (max): 0.87 kA Ib (max): 0.39 kA Vr (max): 253.87 kV Vy (max): 256.06 kV Vb (max): 259.04 kV |

KALPAKKA - 400KV

|  | KALPAKKA - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:09-06-2026 19:26:27.681 Trip L1 CZ Device trip G, Trip L1 G, Trip BBP G, Trip BUS3 G |

400KV/220KV KALPAKKA-ICT-3

|  | KALPAKKA - 400KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:09-06-2026 19:26:27.681 Trip L1 CZ Device trip G, Trip L1 G, Trip BBP G, Trip BUS3 G |

400KV-GAZUWAKA-KALPAKKA-2

|  | GAZUWAKA - 400KV | KALPAKKA - 400KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:09-06-2026 19:26:27.713 DT_REC_CH1/2 GR_A/B_OPTD T_CB_BO T_CB_YO M_CB_RO, M_CB_YO M_CB_BO CB_PD_OPTD T_CB_RO Ir (max): 0.01 kA Iy (max): 1.20 kA Ib (max): 0.84 kA Vr (max): 234.60 kV Vy (max): 238.34 kV Vb (max): 261.50 kV | DR Trigger Time:09-06-2026 19:26:27.681 Trip L1 CZ Device trip G, Trip L1 G, Trip BBP G, Trip BUS3 G |

- A) PMU Analysis:

From the PMU plot, R-G fault can be observed without any delayed fault clearance

B) SCADA Analysis:

From SCADA data, Kalpakka Bus 3 tripping is observed at 19:26 during the event

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):  Nil

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| APTRANSCO | 1. Restoration work attending by O&M wing Kalpakka |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

400KV-SIMHADRI-KALPAKKA-2 charged on 09.06.2026 at 21:21Hrs.

400KV-KALPAKKA-VEMAGIRI_AP-1 charged on 10.06.2026 at 06:41 Hrs

400KV/220KV KALPAKKA-ICT-3 charged on 10.06.2026 at 13:25Hrs

400KV-GAZUWAKA-KALPAKKA-2 charged on 10.06.2026 at 20:01Hrs

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | APTRANSCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 |  |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: