## Summary
सुरक्षा प्रदर्शन सूचकांक/ Protection Performance Indices |  |  |  |  | 01-05-2026 | to | 31-05-2026
उपयोगिता का नाम/Name of the Utility | सुरक्षा अभियान के अनुसार ट्रिपिंग क्रम में/Trippings in order as per protection operation (Nc) | अनुचित परिचालनों की संख्या/No.of Unwarranted Operations (Nu) | विफल परिचालनों की संख्या/No.of failed operations (Nf) | (Ni=Nu+Nf) | सुरक्षा सूचकांक/Security Index [S=Nc/ (Nc+NU)] | निर्भरता सूचकांक/Dependability Index [D=Nc/ (Nc+Nf)] | विश्वसनीयता सूचकांक/Reliability Index [R=Nc/ (Nc+Ni)]
ADANI_APL | 2 | 0 | 0 | 0 | 1 | 1 | 1
APGENCO | 43 | 3 | 1 | 4 | 0.93478 | 0.97727 | 0.91489
APTRANSCO | 375 | 2 | 7 | 9 | 0.99469 | 0.98168 | 0.97656
HINDUJA | 6 | 0 | 0 | 0 | 1 | 1 | 1
JSW_RE | 2 | 0 | 0 | 0 | 1 | 1 | 1
JSW_THERMAL | 0 | 2 | 0 | 2 | 0 | NA | 0
KPCL | 5 | 0 | 0 | 0 | 1 | 1 | 1
KSPDCL | 1 | 0 | 0 | 0 | 1 | 1 | 1
NPCIL_KAIGA | 3 | 0 | 0 | 0 | 1 | 1 | 1
NPCIL_KKNP | 1 | 0 | 0 | 0 | 1 | 1 | 1
NTECL | 6 | 0 | 0 | 0 | 1 | 1 | 1
NTPC_KUDGI | 3 | 0 | 0 | 0 | 1 | 1 | 1
NTPC_RSTPS | 9 | 0 | 0 | 0 | 1 | 1 | 1
NTPC_SIMHADRI | 1 | 0 | 0 | 0 | 1 | 1 | 1
NTPC_TESTPP | 1 | 0 | 0 | 0 | 1 | 1 | 1
OSTRO_KANNADA | 1 | 0 | 1 | 1 | 1 | 0.5 | 0.5
PGCIL SR-1 | 83 | 4 | 1 | 5 | 0.95402 | 0.9881 | 0.94318
PGCIL SR-2 | 120 | 4 | 2 | 6 | 0.96774 | 0.98361 | 0.95238
PONDICHERRY | 2 | 0 | 0 | 0 | 1 | 1 | 1
RENEW POWER PVT LTD | 1 | 0 | 1 | 1 | 1 | 0.5 | 0.5
TANTRANSCO | 324 | 7 | 30 | 37 | 0.97885 | 0.91525 | 0.89751
TATA | 1 | 0 | 0 | 0 | 1 | 1 | 1
TGGENCO | 34 | 1 | 0 | 1 | 0.97143 | 1 | 0.97143
TGTRANSCO | 132 | 6 | 7 | 13 | 0.95652 | 0.94964 | 0.91034
Vena_GadagPS | 2 | 0 | 0 | 0 | 1 | 1 | 1
AMGEPL | NA | NA | NA | NA | NA | NA | NA
BETAMWIND | NA | NA | NA | NA | NA | NA | NA
GREENKO | NA | NA | NA | NA | NA | NA | NA
GRT | NA | NA | NA | NA | NA | NA | NA
KLEIO_SOLAR | NA | NA | NA | NA | NA | NA | NA
MEPL | NA | NA | NA | NA | NA | NA | NA
NTPL | NA | NA | NA | NA | NA | NA | NA
ORANGE | NA | NA | NA | NA | NA | NA | NA
PVG_IRCON_S | NA | NA | NA | NA | NA | NA | NA
SEIL | NA | NA | NA | NA | NA | NA | NA
SERENTICA_RI1PL | NA | NA | NA | NA | NA | NA | NA
Spring_Pugalur | NA | NA | NA | NA | NA | NA | NA
TELENGANA | NA | NA | NA | NA | NA | NA | NA
ADANI_ATL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
APSPCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
Ayana Renewable Power Six Pvt Ltd | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
BHAVINI | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
GREENINFRA | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
HIRIYUR_ZREPL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
ILFS | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
INDIGRID | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
KPTCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
KSEB | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
LKPPL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
MYTRAH | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
NLC | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
NPCIL_MAPS | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
NTPC | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SAEL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SCCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SEPC | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
SEPL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
TNGECL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified
TNPGCL | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified | Not Verified

## All
क्र. स. /S.NO. | एलमन्ट नाम/ ELEMENT NAME | एलमन्ट प्रकार/ELEMENT TYPE | वोल्टेज स्तर/Voltage Level | इंट्रा/इंटर स्टेट एलमन्ट/Intra/Inter state element | एलीमेंट का मालिक/Owner of the element | ट्रिपिंग की तारीख/ TRIPPING DATE | ट्रिपिंग का समय/ TRIPPING TIME | भेजनेवाला/Sending End |  |  |  |  | प्राप्त करनेवाला/Receiving End |  |  |  |  | ट्रिपिंग का कारण /REASON for Tripping
[8 empty] | मालिक/OWNER | वर्गीकरण/Classification | वर्गीकरण टिप्पणी/Classification Comment | कार्य योजना/Action Plan | कार्य योजना की स्थिति/Action Plan Status | मालिक/OWNER | वर्गीकरण/Classification | वर्गीकरण टिप्पणी/Classification Comment | कार्य योजना/Action Plan | कार्य योजना की स्थिति/Action Plan Status
1 | 230KV-ACHARAPAKAM-VILLUPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-05-2026 | 13:25 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,Y,N,LOCK OUT | Carrier signal has to be checked at Villupuram end. | Pending | TRANSIENT FAULT
2 | 230KV-VEERAPURAM-CUDDALORE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-05-2026 | 02:46 | TANTRANSCO | Correct Operation | idly charged from Cuddalore |  |  | TANTRANSCO | Correct Operation | ZONE.2,R,N |  |  | TRANSIENT FAULT
3 | 220KV-NAGJHERI-BIDNAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 13-05-2026 | 17:22 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone-1, R-phase, Ia=15.13kA, distance=1.73km |  |  | Transient fault
4 | 230KV-ALAGAR_KOVIL-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-05-2026 | 23:23 | TANTRANSCO | Failure Operation | ZONE.1,R,N,LOCKOUT due to carrier fail | OLTE defect has to be attended at Alagarkoil end | Pending | TANTRANSCO | Failure Operation | ZONE.1,R,N,LOCKOUT due to carrier fail | OLTE defect has to be attended at Alagarkoil end | Pending | TRANSIENT FAULT
5 | 230KV-ALAGAR_KOVIL-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-05-2026 | 23:41 | TANTRANSCO | Failure Operation | ZONE.1,R,N,AR LOCKOUT | OLTE defect has to be attended at Alagarkoil end | Pending | TANTRANSCO | Failure Operation | ZONE.1,R,N,AR LOCKOUT | OLTE defect has to be attended at Alagarkoil end | Pending | TRANSIENT FAULT
6 | 230KV-ALAGAR_KOVIL-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-05-2026 | 18:41 | TANTRANSCO | Failure Operation | ZONE.1,R,N,LOCKOUT | OLTE defect has to be attended at Alagarkoil end | Pending | TANTRANSCO | Failure Operation | ZONE.1,R,N,LOCKOUT | OLTE defect has to be attended at Alagarkoil end | Pending | TRANSIENT FAULT
7 | 230KV-METTURAUTO-HOSUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 31-05-2026 | 22:48 | TANTRANSCO | Failure Operation | ZONE.1,R,N,LOCKOUT_due to carrier fail | Healthiness of carrier has to be checked | Pending | TANTRANSCO | Failure Operation | ZONE.1,R,N,LOCKOUT_due to carrier fail | Healthiness of carrier has to be checked | Pending | TRANSIENT FAULT
8 | 230KV-KORATTUR-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-05-2026 | 22:26 | TANTRANSCO | Unwanted Operation | over reached tripping for line fault in 230kV Manali - Central CMRL feeder | resistive reach setting revised and tested | Completed | TANTRANSCO | Correct Operation | holding
9 | 230KV-KOYAMBEDU_GIS-TIRUVERKADU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 16-05-2026 | 13:07 | TANTRANSCO | Correct Operation | Zone.1,B,N,AR OFF _ Composite feeder |  |  | TANTRANSCO | Correct Operation | CAT,B,N,Lockout_ AR OFF _ Composite feeder
10 | 220KV-NAGJHERI-BIDNAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 14-05-2026 | 22:26 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone-1, R-phase, distance=13.9km,, Ia=7.016kA |  |  | Transient fault
11 | 230KV-NCTPS-KILPAUK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-05-2026 | 12:52 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N, Lockout_ AR OFF_composite feeder |  |  | TRANSIENT FAULT
12 | 230KV-NCTPS-KILPAUK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-05-2026 | 12:05 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TRANSIENT FAULT
13 | 220KV-BTPS-LINGAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 03-05-2026 | 15:53 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone-1, Y & B-phase, distance=16.81km, AR lock out due to phase phase fault |  |  | Transient fault involving Y&B phases
14 | 230KV-THARAMANI-SHOLINGANALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-05-2026 | 14:04 | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | R Phase Jumper cut at location no:54
15 | 400KV-PALAVADI-RASIPALYAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 02-05-2026 | 16:20 | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
16 | 400KV-ALAMATHY-TIRUVALAM_TN-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 16:05 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
17 | 400KV-ARIYALUR-KALVENDAPATTU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 06-05-2026 | 03:53 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | PGCIL SR-2 | Correct Operation | AR Successful both ends on Bph-G transient Fault in Line. 22.6 km/ 9.35 kA. |  |  | AR Successful both ends on Bph-G transient Fault in Line
18 | 220KV-LINGSUGUR-RTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 23-05-2026 | 20:25 | KPTCL | Correct Operation | Zone-1, B-phase, distance=58.34km, Ib=2.601kA. AR opearted |  |  | KPCL |  |  |  |  | AR operated and successful at Lingasugur
19 | 400KV-KARAMADAI-MTPS_ST_III-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 06-05-2026 | 19:22 | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
20 | 220KV-ALMATTI-BASAVANA_BAGEWADI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 17-05-2026 | 15:00 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone- 2, Y-phase, IB-2.958kA, Distance-30.44km |  |  | Transient fault
21 | 400KV-VALLUR-ALAMATHY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 08-05-2026 | 02:39 | NTECL |  |  |  |  | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
22 | 220KV-VARAHI-KEMAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 12-05-2026 | 21:20 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone-1, R-Y Phase, distance=17.97km, Ia=3.027kA, Ib=5.24KA |  |  | Transient fault due to lightning.
23 | 400KV-ARIYALUR-KALVENDAPATTU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 09-05-2026 | 11:15 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | PGCIL SR-2 | Correct Operation | AR Successful both ends Bph-G Fault in Line. 37.4 km /6.16 kA |  |  | AR Successful both ends Bph-G Fault in Line.
24 | 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 11-05-2026 | 20:12 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
25 | 220KV-VARAHI-KEMAR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 14-05-2026 | 17:31 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone-2, YB fault. distance=65.18km, Ia=24.65A, Ib=2.48KA, Ic=2.47KA |  |  | Transient fault suspected due to heavy rain and lightning
26 | 400KV-SHOLINGANALLUR-KALVENDAPATTU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 13-05-2026 | 00:54 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | PGCIL SR-2 | Correct Operation | AR Successful both ends . - 2.1 km /17.59 kA. |  |  | AR Successful both ends Yph-G Fault in Line.
27 | 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 14-05-2026 | 12:32 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
28 | 220KV-HASSAN-DUDDA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 03-05-2026 | 10:56 | PGCIL SR-2 |  |  |  |  | KPTCL | Correct Operation | R-Phase Jump cut at tower loc No. 12 |  |  | Distance protection : Zone-1, R-ph , at 20.29km , Fault Current 2.37kA.
29 | 400KV-ARIYALUR-KALVENDAPATTU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 19-05-2026 | 20:23 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | PGCIL SR-2 | Correct Operation | AR Successful both ends on Rph-G Fault in Line. |  |  | AR Successful both ends on Rph-G Fault in Line.
30 | 220KV-KEMAR-KAVOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 06-05-2026 | 11:25 | KPTCL | Correct Operation | Zone-1, RY ph distance 27.41km , Fault Current IR =3.31kA, IY=3.076kA |  |  | KPTCL | Correct Operation | Zone-1, RY ph distance 16.37km , Fault Current IR =2.283kA, IY=3.066kA |  |  | Coconut tree branches at loc. No. 91,92 removed by availing LC and line charged. Lock out operated at both ends.
31 | 400KV-PUGALUR-VELLALAVIDUTHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 28-05-2026 | 19:06 | PGCIL SR-2 | Correct Operation | AR Successful . Pugalur end=137 km / 3.2 kA |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | AR Successful both ends on Rph-G transient Fault in Line.
32 | 400KV-PALAVADI-RASIPALYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 29-05-2026 | 18:10 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
33 | 220KV-BELAGAVI-AEQUES-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 07-05-2026 | 03:56 | KPTCL | Correct Operation | Zone-1, B-N phase, Dist=22.09km, Fault current: Ic=3.746kA, TOR due to persistent fault |  |  | KPTCL | Correct Operation | Zone-1, B-N phase, Dist=9.577km, Fault current: Ic=4.235kA, TOR due to persistent fault |  |  | Insulator decap at Location No.58
34 | 230KV-THUDIYALUR-KARAMADAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 14:59 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
35 | 230KV-MILAVITTAN-Chekkanurani-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TNEB | 02-05-2026 | 21:02 | TANTRANSCO | Failure Operation | ZONE.1,Y,N_ AR KEPT OFF_ DURING THE INCIDENT HENCE LOCKOUT TRIP | AR Kept inservice | Completed | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TRANSIENT FAULT
36 | 220KV-VEMAGIRI_AP-PEDDAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 12:54 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
37 | 230KV-MILAVITTAN-Chekkanurani-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TNEB | 04-05-2026 | 05:54 | TANTRANSCO | Failure Operation | ZONE.1,Y,N_AR KEPT OFF During the incident hence Lockout trip initiated | AR kept in service | Completed | TANTRANSCO | Correct Operation | ZONE.Y,N_TOR |  |  | TRANSIENT FAULT
38 | 220KV-NAGJHERI-BIDNAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 11-05-2026 | 17:40 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone1, R-ph, fault current 2.09kA, 68.11km |  |  | Insulator decap at Loc No. 32, AR operated in first cycle but tripped during reclaim time due to persisting fault.
39 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-05-2026 | 09:47 | TANTRANSCO | Correct Operation | CAT,B,N _TOR | REASON FOR ZONE.1 OPERATION HAS TO BE CHECKED |  | TANTRANSCO | Failure Operation | Main.1 relay sensed the fault in reverse zone but main.2 relay sensed the fault in Zone.1 | Main.2 relay ( Micom P442) has to be checked | Pending | B phase Busbar protection operated due to cut in B Phase jumper in 230 kV Karaikudi 1# breaker towards the Isolator(229AT)
40 | 220KV-Renew_Surya_Ojas_Koppal_W-KOPPAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | RSOPL | 15-05-2026 | 05:20 | RENEW POWER PVT LTD | Failure Operation | Transient B-Phase to ground fault on 220kV Line. Line Protection operated correctly and Tripped the Breaker. AR scheme failed to operate at Local End, Whereas AR was successful at remote end. Line restored manually after inspection | Discussion is going on with OEM Team for check the logic of AR scheme and also we will conduct the AR test by deployed OEM team in the month of October 2026 | Pending | INDIGRID |  |  |  |  | RSOPL Koppal 220kV line 201 Bay Tripped on R-Phase Ground distance protection during Heavy rain and lightning nearby site areas
41 | 230KV-MILAVITTAN-Chekkanurani-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TNEB | 29-05-2026 | 10:37 | TANTRANSCO | Correct Operation | ZONE.1,R,Y_LOCKOUT |  |  | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | At Loc 33 , Y phase Jumper cut & fell on R phase
42 | 220KV-HIRIYUR_OSTRO-HIRIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | RENEW POWER PVT LTD | 18-05-2026 | 21:28 | OSTRO_KANNADA | Failure Operation | Transient B-Phase to ground fault on 220kV Line. Line Protection operated correctly and Tripped the Breaker. AR scheme failed to operate at Local End, Whereas AR was successful at remote end. Line restored manually after inspection | Discussion is going on with OEM Team for check the logic of AR scheme and also we will conduct the AR test by deployed OEM team in the month of October 2026 | Pending | PGCIL SR-2 |  |  |  |  | Hiriyur _Ostro Kannada -220Kv Line tripped due to R Phase to ground fault(Fault current-1.257 kA) 13.7Km Distance during heavy lightening and rain condition
43 | 765KV-KURNOOL_PG-NPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | POWERGRID | 28-05-2026 | 20:08 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | Line A/R Successful on B-G Fault.
44 | 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 28-05-2026 | 19:09 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | Line A/R successful on R-G fault.
45 | 400KV-NAGARJUNASAGAR_PG-RAMAGUNDAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 28-05-2026 | 18:22 | PGCIL SR-1 | Correct Operation |  |  |  | NTPC_RSTPS |  |  |  |  | Line A/R successful on Y-G fault.
46 | 400KV-CUDDAPAH-NP_KUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 26-05-2026 | 20:17 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | A/R successful on R-G fault.
47 | 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | PVTL | 25-05-2026 | 16:35 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | Line Auto reclosed successfully on R-N fault
48 | 220KV-SIRSI-SHARAVATHY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 12-05-2026 | 19:22 | KPTCL | Correct Operation | Zone 1, B-phase, distance=21.9km, Ib=1.46kA, TOR at Shimoga end |  |  | KPCL |  |  |  |  | Top phase insulator flashed at Loc. 94.
49 | 400KV-PUGALUR HVDC-ARASUR_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 02-05-2026 | 16:24 | PGCIL SR-2 | Correct Operation | Line autoreclosed succesfully on R -G fault.- 5.6 km / 23.27 kA |  |  | PGCIL SR-2 | Correct Operation | Line autoreclosed succesfully on R -G fault. 61.0 km / 5.2 kA |  |  | Line autoreclosed succesfully on R -G fault
50 | 220KV-SIRSI-SHARAVATHY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 16-05-2026 | 19:00 | KPTCL | Correct Operation | Zone-1, Y-B phase, Ib-3.34kA, Ic-3.346kA, distance=18.90km, |  |  | KPCL |  |  |  |  | Top phase insulator de-capped at Location No. 116.
51 | 400KV-NAGAPATTNAM_PS-NEYVELI_TS1_EXP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 12:39 | PGCIL SR-2 | Correct Operation | Line autoreclosed succesfully both ends on R-G fault. 2.49 km / 14.38 kA. |  |  | NLC |  |  |  |  | Line autoreclosed succesfully both ends on R-G fault.
52 | 400KV-CUDDAPAH-TUMKUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | PSITSL | 01-05-2026 | 00:45 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-2 |  |  |  |  | Auto reclose successful on Rph-G fault.
53 | 400KV-SALEM-NNTPP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 21:52 | PGCIL SR-2 | Correct Operation | AR Successful - 52.2 km /5.88 kA |  |  | NLC | Correct Operation |  |  |  | Line autoreclose successful both ends on Y-G Fault.
54 | 220KV-VARAHI-MRS SHIMOGA-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 16-05-2026 | 20:04 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone-1, B-Phase, Carrier aided protection trip, Ic-1.805kA, diastnce=93.93km, AR unsuccessful due to persistent fault |  |  | Dry areca nut tree fall in between Location No. 58 & 59
55 | 400KV-TUTICORIN_PS-DHARMAPURI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 06-05-2026 | 19:58 | PGCIL SR-2 | Correct Operation | AR Successful - 342.1 km /1.28 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful - 56.8 km / 5.63 KA. |  |  | Line autoreclose successful both ends on Y-G Fault
56 | 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | PVTL | 03-05-2026 | 16:49 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | A.R operated successfully on B-N Fault
57 | 400KV-MADURAI_PG-PUGALUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 08-05-2026 | 06:14 | PGCIL SR-2 | Correct Operation | Line A/R successful on B -G fault.- 50.72 / 5.7 kA |  |  | PGCIL SR-2 | Correct Operation | Line A/R successful on B -G fault.- 70.5 km / 4.8 kA. |  |  | Line A/R successful on B -G fault.
58 | 400KV-GOOTY-NPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 21:41 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | A/R successful R-N Fault
59 | 400KV-KALVENDAPATTU-VALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 08-05-2026 | 09:11 | PGCIL SR-2 | Correct Operation | AR Successful - 122 km / 2.5 kA. |  |  | NTECL |  |  |  |  | Line autoreclosed successfully on R-G fault
60 | 220KV-TUBINAKERE-CHANNAPATNA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 22-05-2026 | 02:18 | KPTCL | Correct Operation | Zone -1, R-phase, Ia=3.344kA, distance=34.64 km |  |  | KPTCL | Correct Operation | Zone -1, R-phase, Ia-3.347kA, distance=23.32km |  |  | Insulator faulty b/n tower location No. 200 & 267. after replacement of insulator test charged stood ok
61 | 400KV-NAGAPATTNAM_PS-NEYVELI_TS1_EXP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 08-05-2026 | 09:12 | PGCIL SR-2 | Correct Operation | AR Successful - 4.59 km / 11.28 kA. |  |  | NLC |  |  |  |  | Line autoreclosed successfully both ends on R-G fault
62 | 400KV-KALVENDAPATTU-VALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 09-05-2026 | 04:57 | PGCIL SR-2 | Correct Operation | AR Successful - 128.2 km / 2.39 kA. |  |  | NTECL |  |  |  |  | Line Auto Reclosed on R-G fault at both ends
63 | 400KV-CUDDAPAH-NAGARJUNASAGAR_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 07-05-2026 | 16:46 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | A/R successful B-N fault
64 | 400KV-NNTPP-PUDUCHERRY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 11-05-2026 | 10:05 | NLC |  |  |  |  | PGCIL SR-2 | Correct Operation | AR Successful - 28.4 km /3.86 kA. |  |  | Line auto reclosed succcessfully both ends on Y -G fault.
65 | 400KV-PUGALUR HVDC-THIRUVALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 10-05-2026 | 22:55 | PGCIL SR-2 | Correct Operation | AR Successful - 376.6 km / 1.06 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful - 46 km / 7.11 kA. |  |  | Line auto reclosed successfully both ends on Y-G fault.
66 | 400KV-KHAMMAM_PG-WARANGAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 10-05-2026 | 14:00 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | A/R successful on R-G fault
67 | 400KV-NARENDRA-GUTTUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-05-2026 | 05:40 | PGCIL SR-2 | Correct Operation | AR Successful - 47.89 km / 4.9 kA. |  |  | KPTCL | Correct Operation |  |  |  | Auto reclosed successfully on Bph-G (Ph-earth) transient fault
68 | 765KV-NIZAMABAD-WARDHA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | POWERGRID | 13-05-2026 | 22:58 | PGCIL SR-1 | Correct Operation | [8 empty] | A/R successful on R-G fault
69 | 400KV-MYSORE-KOZHIKODE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 18-05-2026 | 06:19 | PGCIL SR-2 | Correct Operation | AR Successful - 156.5 km / 1.83 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful - 30.37 km / 5.31kA. |  |  | Line Auto reclosed successfully on Yph-N (Ph-earth) transient fault
70 | 400KV-HIRIYUR-MYSORE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-05-2026 | 18:42 | PGCIL SR-2 | Correct Operation | AR Successful - 37.48 km / 7.45 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful - 131.6 km / 1.98 kA. |  |  | Auto reclosed successfully on B-N (Ph-earth) transient fault
71 | 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | POWERGRID | 16-05-2026 | 15:41 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | Auto Reclose successfully operated on R-G fault
72 | 400KV-KALVENDAPATTU-VALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-05-2026 | 23:03 | PGCIL SR-2 | Correct Operation | AR Successful -45.6 km / 5.85 kA. |  |  | NTECL |  |  |  |  | Line Auto reclose successful both ends on R-G Fault.
73 | 765KV-RAICHUR_PG-SHOLAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | RSTCL | 18-05-2026 | 20:10 | PGCIL SR-1 | Correct Operation | [8 empty] | A/R successful B-N fault
74 | 400KV-PAVAGADA_PG-TUMKUR-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-05-2026 | 23:39 | PGCIL SR-2 | Correct Operation | AR Successful -24.3 km / 9.89 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful -81.6 km / 3.88 kA. |  |  | Line Auto reclose successful both ends on R-G Fault.
75 | 400KV-GOOTY-PAVAGADA_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 20-05-2026 | 17:00 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-2 |  |  |  |  | Line A/R successful on R-G fault.
76 | 400KV-KUDGI_PG-NARENDRA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-05-2026 | 16:38 | PGCIL SR-2 | Correct Operation | AR Successful -70.6 km / 5.08 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful -95.8 km / 3.39 kA. |  |  | Auto reclosed successfully both ends on B-N (Ph-earth) transient fault
77 | 765KV-SRIKAKULAM-ANGUL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | POWERGRID | 21-05-2026 | 16:40 | PGCIL SR-1 | Correct Operation | [8 empty] | Auto Reclosed successfully on B-N fault.
78 | 400KV-MADURAI_PG-TUTICORIN_PS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 23-05-2026 | 18:58 | PGCIL SR-2 | Correct Operation | AR Successful -61.19 km / 5.94 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful -31.3 km / 8.87 kA. |  |  | Line Auto reclosed successful both ends on B-G Fault.
79 | 765KV-CHILAKALURIPETA-CUDDAPAH-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | PSITSL | 22-05-2026 | 00:32 | PGCIL SR-1 | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | Auto Reclosed successfully on R-N fault.
80 | 400KV-TUTICORIN_PS-DHARMAPURI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 24-05-2026 | 19:40 | PGCIL SR-2 | Correct Operation | AR Successful -457.5 km / 1.25 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful - 29.6 km / 9.51kA. |  |  | Line auto reclosed successfully both ends on Y-G fault
81 | 400KV-GHANAPUR-RAMAGUNDAM-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 23-05-2026 | 18:13 | PGCIL SR-1 | Correct Operation |  |  |  | NTPC_RSTPS |  |  |  |  | Line Auto Reclosed Successfully on R-N Fault.
82 | 400KV-PAVAGADA_PG-MYSORE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 29-05-2026 | 23:30 | PGCIL SR-2 | Correct Operation | AR Successful - 7.49 km / 17.35 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful - 319 km / 1.07 kA. |  |  | Line auto reclosed successfully both ends on Y-G fault
83 | 765KV-RAICHUR_PG-SHOLAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | RSTCL | 23-05-2026 | 19:31 | PGCIL SR-1 | Correct Operation | [8 empty] | A/R sucessful B-N fault Fault
84 | 400KV-TUMKUR-YELHANKA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 30-05-2026 | 16:30 | PGCIL SR-2 | Correct Operation | AR Successful - 50.8 km / 6.04 kA. |  |  | PGCIL SR-2 | Correct Operation | AR Successful - 15.2 km / 11.35 kA. |  |  | Line Auto reclosed successfully both ends on R - G fault.
85 | 220KV-ANCHEPALYA-NAGAMANGALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 29-05-2026 | 20:36 | KPTCL | Correct Operation | Zone-1, Y-Phase, distance=44.34km, |  |  | KPTCL | Failure Operation | Zone-1,Y-Phase, distance=25.77km, AR not operated due to carrier fail | Carrier issue has been resolved | Completed | Transient fault involving Y phase AR not operated due to carrier fail
86 | 220KV-ASUPAKA-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 01-05-2026 | 12:40 | TGTRANSCO | Correct Operation | Correcet operation |  |  | APGENCO | Unwanted Operation | y-phase to ground fault at both ends | Carrier signal end to end testing carried out on 05.06.2026 with the co-ordination of APTRANSCO & TGTRANSCO and observed that logic issue at relay in Main-1 at Asupaka end. After rectification of logic issue at Asupaka , the carrier signal end to end testing carriedout and found normal. | Completed | TRIPPED ON Y-N FAULT
87 | 765KV-KURNOOL_PG-CUDDAPAH-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | POWERGRID | 01-05-2026 | 01:59 | PGCIL SR-1 | Correct Operation | NIL |  |  | PGCIL SR-1 | Correct Operation | Feeder tripped on operation of over voltage. The voltage is as per the system conditions |  |  | TRIPPED ON OVER VOLTAGE.
88 | 400KV-GUDIWADA-SATTENPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 01-05-2026 | 12:52 | APTRANSCO | Correct Operation | Fault tripping in Z1 ,R-Phase |  |  | APTRANSCO | Correct Operation | No visible fault observed |  |  | TRIPPED ON R-N FAULT
89 | 400KV-NELLORE_PG-VIJAYAWADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 01-05-2026 | 09:48 | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisting fault |  |  | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisting B-N fault |  |  | B-N fault Vijayawada M1:154.6KM/2.44KA Nellore M1:206.6KM/1.9KA
90 | 220KV-ELAPULLY-PALAKKAD(KL)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 02-05-2026 | 17:06 | PGCIL SR-2 | Correct Operation | Line tripped due to backup DEF trip due to downstream fault uncleared. |  |  | KSEB | Correct Operation | No trip initiated from from Palakkad end, feeder tripped on Direct trip received |  |  | TRIPPED ON DIRECTIONAL EARTH FAULT
91 | 220KV-ELAPULLY-PALAKKAD(KL)-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 02-05-2026 | 17:06 | PGCIL SR-2 | Correct Operation | Line tripped due to backup DEF trip due to downstream fault uncleared. |  |  | KSEB | Correct Operation | No trip initiated from from Palakkad end, feeder tripped on Direct trip received |  |  | TRIPPED ON DIRECTIONAL EARTH FAULT
92 | 220KV-ELAPULLY-PALAKKAD(KL)-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 02-05-2026 | 17:06 | PGCIL SR-2 | Correct Operation | Line tripped due to backup DEF trip due to downstream fault uncleared. |  |  | KSEB | Correct Operation | No trip initiated from from Palakkad end, feeder tripped on Direct trip received |  |  | TRIPPED ON DIRECTIONAL EARTH FAULT
93 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 02-05-2026 | 13:52 | APGENCO | Correct Operation | Correct operation |  |  | TGGENCO | Correct Operation | DEF Protection Operated |  |  | RN fault
94 | 400KV-PUGALUR HVDC-ARASUR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 02-05-2026 | 16:27 | PGCIL SR-2 | Correct Operation | AR was attempted and unsuccessful as the fault was of permanent nature. |  |  | PGCIL SR-2 | Correct Operation | Tripped in reclaim time |  |  | Tripped
95 | 400KV-GHANAPUR-MAMIDAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 02-05-2026 | 14:15 | PGCIL SR-1 | Correct Operation | NA |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON B-N FAULT
96 | 220KV-ANCHEPALYA-NAGAMANGALA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 29-05-2026 | 20:36 | KPTCL | Correct Operation | Y-Phase, distance=44.34km,, IB=2.366kA, |  |  | KPTCL | Failure Operation | Tripped on Y-Phase fault, AR not operated due to carrier fail | Carrier issue has been resolved | Completed | YN fault in Zone-1,AR not operated due to carrier fail
97 | 400KV-KARAMADAI-ARASUR_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 02-05-2026 | 15:17 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | PGCIL SR-2 | Correct Operation | Tripped in reclaim time |  |  | BN fault
98 | 400KV-PUGALUR HVDC-ARASUR_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 02-05-2026 | 16:26 | PGCIL SR-2 | Correct Operation | AR was attempted but line tripped as the fault was of permanent nature. |  |  | PGCIL SR-2 | Correct Operation | Tripped in reclaim time |  |  | Tripped
99 | 230KV-TTGS-JSW_Vilathikulam_300MW-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | JINDAL | 02-05-2026 | 18:39 | PGCIL SR-2 | Unwanted Operation | Rph to Earth fault Differential operated | DT sent during single phase fault issue in Logic Bays belongs to JSW Vilathikulam. OEM engineer to be deputed by M/s JSW- Vilathikulam. | Pending | JSW_RE | Correct Operation | Nil |  |  | RN fault
100 | HVDC 800KV PUGALUR HVDC Pole 1 | HVDC POLE | HVD | Intra | POWERGRID | 03-05-2026 | 00:54 | PGCIL SR-2 | Correct Operation | Raigarh Pugalur Line-1 (Pole-1 & Pole-3) tripped at both end due to DVD Measurement error at Raigarh end. | [7 empty] | DC line protection fault at HVDC Raigarh
101 | 400KV-GUDIWADA-SATTENPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 02-05-2026 | 12:47 | APTRANSCO | Correct Operation | Fault tripping in Z1 ,R-Phase |  |  | APTRANSCO | Correct Operation | single line to ground fault |  |  | TRIPPED DUE TO R-N FAULT
102 | 400KV-ALAMATHY-TIRUVALAM_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 15:56 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR Lockout due to subsequent fault within reclaim time_ Transient fault |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR Lockout due to subsequent fault within reclaim time_ Transient fault |  |  | TRIPPED AND REASON AWAITED
103 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 03-05-2026 | 14:08 | TGGENCO | Correct Operation | TRIP ABC; START C,N; 47.89KM; 3.19KA |  |  | APTRANSCO | Correct Operation | Due to heavy wind & rain at KTPS End. Patrolling done & Taurus test conducted by TG Lines Wing. |  |  | SOTF OPERATED
104 | 220KV-ASUPAKA-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 03-05-2026 | 12:29 | TGTRANSCO | Correct Operation | Correcet operation |  |  | APGENCO | Failure Operation | The 220 KV LS-ASPK feeder tripped at Lower Sileru end and Asupaka end auto reclosure Successfully | Carrier signal end to end testing carried out on 05.06.2026 with the co-ordination of APTRANSCO & TGTRANSCO and observed that logic issue at relay in Main-1 at Asupaka end. After rectification of logic issue at Asupaka , the carrier signal end to end testing carried out and found normal. | Completed | Tripped on R-N fault (lower sileru end R-N zone 2 lower sileru-asupaka 42.km (aspk end) Main1: 1.4 kA)
105 | 400KV-DICHPALLY-RAMAGUNDAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 03-05-2026 | 14:33 | TGTRANSCO | Correct Operation | Correcet operation |  |  | NTPC_RSTPS | Correct Operation | correct operation |  |  | Rph, DPR operated
106 | 400KV-MALKARAM-SURYAPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 03-05-2026 | 15:29 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED AND REASON AWAITED
107 | 400KV-MALKARAM-SURYAPET-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 03-05-2026 | 15:54 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED AND REASON AWAITED
108 | HVDC 800KV PUGALUR HVDC Pole 3 | HVDC POLE | HVD | Intra | POWERGRID | 03-05-2026 | 00:54 | PGCIL SR-2 | Correct Operation | Raigarh Pugalur Line-1 (Pole-1 & Pole-3) tripped at both end due to DVD Measurement error at Raigarh end. | [7 empty] | DC line protection fault at HVDC Raigarh
109 | 400KV-NELLORE_PG-NPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 21:32 | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisting R-N Fault |  |  | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisting R-N fault |  |  | TRIPPED ON R-N FAULT
110 | 132KV-KODADA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 03-05-2026 | 17:57 | TGTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | Rph fault
111 | 400KV-VIJAYAWADA-NELLORE_AP-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 21:33 | PGCIL SR-1 | Correct Operation | A/R attempted and tripped due to fault in reclaim time |  |  | APTRANSCO | Correct Operation | Tripping is due to heavy rain & wind |  |  | TRIPPED DUE TO R-N FAULT
112 | 400KV-NELLORE_PG-THIRUVALAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 03-05-2026 | 21:35 | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisting R-N fault |  |  | PGCIL SR-2 | Correct Operation | DT Received from other end |  |  | B-N fault, NPS :5.75KM / 20.83KA
113 | 765KV-KURNOOL_PG-CUDDAPAH-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | POWERGRID | 03-05-2026 | 22:25 | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisitng fault |  |  | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisting fault |  |  | R-N fault. Fault details KDP M1:20.5KM/8.13KA
114 | 220KV-HIRIYUR-HIRIYUR_KAR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KARNATAKA | 05-05-2026 | 11:41 | PGCIL SR-2 | Correct Operation | Line tripped @ KPTCL end only. No tripping/fault @ POWERGRID end. |  |  | KPTCL | Unwanted Operation | Spurious tripping due to 96 relay mal operation at Hiriyur KA end | Problem with 96 busbar trip relay attended | Completed | Spurious tripping due to 96 relay mal operation at Hiriyur KA end
115 | 220KV-HASSAN-HASSAN-KA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 04-05-2026 | 16:26 | PGCIL SR-2 | Correct Operation | AR attempted tripped on TOR due to Line fault persisting. 28km/5.2ka |  |  | KPTCL | Correct Operation | BN fault, TOR due to persistent fault |  |  | Bph-G fault. Insulator failed at tower Location 53
116 | 400KV-SURYAPET-KETHIREDDYPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 03-05-2026 | 16:13 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON Y-N FAULT
117 | 400KV-KARAIKUDI-KAMUDHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 02-05-2026 | 20:38 | PGCIL SR-2 | Correct Operation | AR Attempt and AR successful |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | R-Y-N FAULT
118 | 765KV-CUDDAPAH-THIRUVALAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | POWERGRID | 03-05-2026 | 22:25 | PGCIL SR-1 | Correct Operation | A/R attempted and tripped on persisting fault |  |  | PGCIL SR-2 | Correct Operation | A/R attempted and tripped on persisting fault |  |  | R-N fault. Fault details KDP M1:20.7 KM/8.49KA
119 | 400KV-ARIYALUR-PUGALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 04-05-2026 | 20:34 | TANTRANSCO | Failure Operation | ZONE.1R,N,AR LOCKOUT_Due to carrier fail | Carrier scheme checked on 06-05-2026 | Completed | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct- AR Successful @ Pugalur( Karur) end. |  |  | TN: R-N, Z-1, 17.75 kA; AR successful at PG
120 | 220KV-HUBLI-SIRSI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 08-05-2026 | 14:46 | KPTCL | Correct Operation | No tripping as the CB is in Hand Trip Condition, idle line |  |  | KPTCL | Correct Operation | Zone-1, R-phase, IA=5.03kA, distance=19.25km. TOR due to persistant fault |  |  | Transient fault, No visible fault found to TLM staff during patrolling. Line charged & stood OK.
121 | 400KV-ARIYALUR-PUGALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 05-05-2026 | 19:02 | TANTRANSCO | Failure Operation | ZONE.1,R,N_LOCKOUT_Due to carrier fail. Location No:551 , to Location 553 earth wire cut. After Earth wire removed the line test Charged stood ok\ | Carrier scheme checked on 06-05-2026 | Completed | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct.AR successful @ Pugalur end |  |  | Tripped
122 | 400KV-SURYAPET-KV_KOTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 03-05-2026 | 17:38 | TGTRANSCO | Correct Operation | Correcet operation |  |  | APTRANSCO | Correct Operation | Zone 2 Rph to G fault with carrier receive . A/R attempted but tripped due to persistent fault |  |  | Reason awaited
123 | 400KV-SURYAPET-KV_KOTA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 03-05-2026 | 18:05 | TGTRANSCO | Correct Operation | Correcet operation |  |  | APTRANSCO | Correct Operation | zone 2 Bph to G fault with Carrier Receive. Auto Recloser was succesful in the first instance of the fault. but feeder tripped for the second fault i.e. within reclaim time. |  |  | TRIPPED ON OVER VOLTAGE.
124 | HVDC 800KV PUGALUR HVDC Pole 2 | HVDC POLE | HVD | Intra | POWERGRID | 05-05-2026 | 20:43 | PGCIL SR-2 | Correct Operation | Pugalur end - All poles are in service. | [7 empty] | Trip
125 | 400KV-KARAIKUDI-MADURAI_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 06-05-2026 | 00:05 | PGCIL SR-2 | Correct Operation | Line tripped on OV-STg-2 Trip during AR Dead time. |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | TRIPPED ON Y-N FAULT
126 | 400KV-URAVAKONDA-MEHBOOBNAGAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 06-05-2026 | 11:03 | APTRANSCO | Correct Operation | enquired other end found no fault hence the feeder was taken into service |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON B-N FAULT
127 | 400KV-ALAMATHY-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 06-05-2026 | 13:10 | TANTRANSCO | Correct Operation | ZONE.1,B,N, TOR_At loc.132, Cph suspension insulator flashover |  |  | TANTRANSCO | Correct Operation | Zone.1,B,N,TOR_At loc.132, Cph suspension insulator flashover |  |  | TRIPPED AND REASON AWAITED
128 | 400KV-NARNOOR-JAMMALAMADUGU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 06-05-2026 | 19:25 | APTRANSCO | Correct Operation | Feeder tripped on Distance Protection |  |  | APTRANSCO | Correct Operation | trip in order |  |  | Tripped on Y-B-N Fault
129 | 400KV-NARNOOR-JAMMALAMADUGU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 06-05-2026 | 19:25 | APTRANSCO | Correct Operation | Feeder tripped on Distance Protection |  |  | APTRANSCO | Correct Operation | trip in order |  |  | Tripped on Y-B-N Fault
130 | 400KV-NELLORE_AP-VTPS_IV-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 21:33 | APTRANSCO | Correct Operation | Tripping is due to heavy rain & wind |  |  | APGENCO | Correct Operation | Correct Operation |  |  | TRIPPED DUE TO R-N FAULT
131 | 400KV-KARAMADAI-MTPS_ST_III-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 06-05-2026 | 19:55 | TANTRANSCO | Correct Operation | CAT,Y,B |  |  | TNPGCL | Correct Operation | AR lockout due to Z1 Phase to Phase Fault. |  |  | Tripped on Y-B Fault
132 | 400KV-NCTPS_STAGE_II-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 07-05-2026 | 06:03 | TNPGCL | Correct Operation | nil |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR_At loc.179, Yph suspension insulator flashover |  |  | B-N FAULT
133 | 132KV-MADIRA-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 07-05-2026 | 21:09 | TGTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | Rph fault
134 | 220KV-KURNOOL_PG_III-SAEL2-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | SAEL | 06-05-2026 | 19:42 | PGCIL SR-1 | Correct Operation | Tripped on LLL fault |  |  | SAEL | Correct Operation | BOTH AT PGCIL END AND SITE LINE DIFFERENTIAL OPERATED. |  |  | TRIPPED ON Y-N FAULT
135 | 400KV-SURYAPET-KETHIREDDYPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 04-05-2026 | 15:04 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | 3ϕ fault. SOTF Operated.
136 | 400KV-KURNOOL_PG-NAGARJUNASAGAR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 18:03 | PGCIL SR-1 | Correct Operation | Tripped on operation of over voltage. DR shared |  |  | PGCIL SR-1 | Correct Operation | NA |  |  | Tripped on Over Voltage
137 | 220KV-UDUMALPET-Pallivasal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KSEB | 01-05-2026 | 03:26 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | KSEB | Correct Operation | AR OPERATED |  |  | AR OPERATED
138 | 220KV-IDDUKI-KALAMASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 02-05-2026 | 15:50 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
139 | 220KV-IDDUKI-KALAMASSERY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 02-05-2026 | 15:50 | KSEB | Correct Operation | AR |  |  | KSEB | Correct Operation | AR |  |  | AR OPERATED
140 | 220KV-EDAMON-SABARIGIRI-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 02-05-2026 | 16:48 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
141 | 220KV-EDAMON-SABARIGIRI-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 02-05-2026 | 17:14 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | AR/LO.CONDUCTOR SNAPPING AT LOC.93/94 |  |  | M1:DP:pickup Y, pickup B, Z1,34km M2:DP:pickup Y, pickup B, Z1,14km
142 | 220KV-BRAHMPURAM-LOWER PERIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 04-05-2026 | 17:04 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | DISC FLASH AT LOC.85 |  |  | ANN: M1 M2 DP optd M1: DP: C-G, Z1, 26.798KM M2: DP: C-G, Z1, 27.074KM
143 | 220KV-IDDUKI-NEW PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 04-05-2026 | 17:24 | KSEB | Failure Operation | PD OPERATED. | PD RELAY TIME ADJUSTED | Completed | KSEB | Correct Operation | AR |  |  | M1: Z1 M2: ZONE-1 Trip, R-phase fault,start phase AN,tripped phase ABC,fault location-10.32km,
144 | 220KV-EDAMON-SABARIGIRI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 07-05-2026 | 18:23 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
145 | 220KV-IDDUKI-PALLIVASAL_EXTN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 07-05-2026 | 16:46 | KSEB | Correct Operation | MULTI PHASE FAULT |  |  | KSEB | Correct Operation | MULTI PHASE FAULT |  |  | Ann: M1 M2 optd M1: Phase A,Phase B,Phase C , Zone -1,TYPE-AB G,Location 32 Km M2: Zone -1,B Phase Fault,Start phase ABN,tripped phase ABC
146 | 765KV-ARIYALUR-NCPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 08-05-2026 | 09:28 | TANTRANSCO | Correct Operation | zone.1,Y,N, Lockout trip due to subsequent fault within reclaim time_At loc 223 and 327 Yph suspension insulator flashover |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N AR SUCCESSFUL & 3 PH TRIP_At loc 223 and 327 Yph suspension insulator flashover |  |  | Tripped
147 | 400KV-GUDIWADA-VEMAGIRI_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 07-05-2026 | 14:48 | APTRANSCO | Failure Operation | Fault tripping in Z1 ,R-Phase | On thorough inspection of the Siemens relay masking configuration, it was observed that the Block Instantaneous SOTF Overcurrent signal corresponding to the Main CB Trip signal, which should have been configured as Low (L), was missing. The configuration has been rectified immediately. The same will be tested as and when LC is taken. | Completed | APTRANSCO | Correct Operation | Single phase to ground fault on the line. AR unsuccessful due to persistent fault. |  |  | GUD: R-N, Z-1, 93 kMs, 2.02 kA; VEM: R-N, Z-1, 27.09 Kms, 9.5 kA
148 | 400KV-NCTPS_STAGE_II-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 08-05-2026 | 02:31 | TNPGCL | Correct Operation | nil |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N.TOR_At loc.180, Yph suspension insulator flashover. |  |  | SOTF OPERATED
149 | 220KV-NP_KUNTA-GALIVVEDU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APSPCL | 08-05-2026 | 13:51 | PGCIL SR-1 | Correct Operation | No tripping at NP Kunta end. |  |  | APSPCL | Unwanted Operation | NA |  |  | Tripped. No other relay indications.
150 | 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 08-05-2026 | 10:12 | TNPGCL | Correct Operation | nil |  |  | TANTRANSCO | Correct Operation | zone.1,R,N,TOR_INSULATOR DE-CAP LOC NO.59 |  |  | TRIPPED ON R-N FAULT
151 | 230KV-BASIN_BRIDGE-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:30 | TANTRANSCO | Correct Operation | Zone.3,Y,B |  |  | TANTRANSCO | Correct Operation | FEEDER ALREADY TRIPPED CONDITION |  |  | Trip
152 | 230KV-BASIN_BRIDGE-PULIYANTHOPE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:30 | TANTRANSCO | Correct Operation | HOLDING |  |  | TANTRANSCO | Correct Operation | ZONE.3,Y,B |  |  | Trip
153 | 230KV-BASIN_BRIDGE-PULIYANTHOPE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:30 | TANTRANSCO | Correct Operation | NOLDING |  |  | TANTRANSCO | Correct Operation | ZONE.3,Y,B |  |  | Trip
154 | 400KV-MYSORE-KOZHIKODE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 08-05-2026 | 17:19 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | tripped on R-N Fault
155 | 230KV-NCTPS-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:30 | TNPGCL | Correct Operation | The fault occurred due to the opening of the Basin Bridge SS take-off tower line. Consequently, for the B and C phase line fault in the 230 kV Tondiarpet feeder to Basin Bridge feeders, the Tondiarpet-1 feeder tripped at Zone-3 from the NCTPS-I end during this period.” |  |  | TANTRANSCO | Correct Operation | HOLDING |  |  | Trip
156 | 230KV-NCTPS-SRIPERUMBADUR_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:30 | TNPGCL | Correct Operation | For a single line-to-ground fault in the Y phase, the Y pole opened. Due to a subsequent fault in the B phase within the dead time, a lockout trip was initiated.” |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B_At loc.31 from NCTPS Yph jumper cut |  |  | Trip
157 | 400KV-VALLUR-ALAMATHY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 08-05-2026 | 05:19 | NTECL | Correct Operation | correct operation |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRIPPED AND REASON AWAITED
158 | 230KV-NCTPS-ATHIPATU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:30 | TNPGCL | Correct Operation | HAND TRIP DUE TO RADIAL FEEDER |  |  | TANTRANSCO | Correct Operation | Source failure |  |  | Trip
159 | 230KV-NCTPS-ATHIPATU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:30 | TNPGCL | Correct Operation | HAND TRIP DUE TO RADIAL FEEDER |  |  | TANTRANSCO | Correct Operation | Source failure |  |  | Trip
160 | 230KV-NCTPS-KILPAUK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:30 | TNPGCL | Correct Operation | HAND TRIP DUE TO RADIAL FEEDER |  |  | TANTRANSCO | Correct Operation | Hand tripped |  |  | Trip
161 | 230KV-NCTPS-TONDIARPET-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:30 | TNPGCL | Correct Operation | The fault occurred due to the opening of the Basin Bridge SS take-off tower line. Consequently, for the B and C phase line fault in the 230 kV Tondiarpet feeder to Basin Bridge feeders, the Tondiarpet-2 feeder tripped at Zone-3 from the NCTPS-I end during this period.” |  |  | TANTRANSCO | Correct Operation | HOLDING |  |  | Trip
162 | 230KV-GUMMIDIPOONDI-NCTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:30 | TANTRANSCO | Correct Operation | ZONE.3,Y,B |  |  | TNPGCL | Correct Operation | HOLDING |  |  | Trip
163 | 220KV-ELAPULLY-PALAKKAD(KL)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 09-05-2026 | 00:35 | PGCIL SR-2 | Correct Operation | No tripping/.fault @ POWERGRID end. Line tripped @ KSEB end only. |  |  | KSEB | Unwanted Operation | Isolator maloperation due to dc earth leakage. No CB operation on either end. | it has been proposed to incorporate an additional 52b contact in the negative DC portion of the isolator close/open circuit. | Pending | Tripped due to opening of isolator on unknown reason and needs investigation
164 | 230KV-KUDANKULAM-TTPS | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 17:58 | NPCIL_KKNP |  |  |  |  | TNPGCL |  |  |  |  | Tripped
165 | 400KV-NCTPS_STAGE_II-VALLUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 09-05-2026 | 06:25 | TNPGCL | Correct Operation | nil |  |  | NTECL | Correct Operation | correct operation |  |  | bph fault
166 | 400KV-GUDDIGUDEM-HINDUJA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 09-05-2026 | 09:13 | APTRANSCO | Correct Operation | persistent fault during auto reclosure. Hence AR unsuccessful. |  |  | HINDUJA | Correct Operation | A/R not operated due to time-based AR operation (AR Lockout occurred before re-closing due to under-voltage sensing). |  |  | tripped on R-N Fault
167 | 220KV-EDAMON-KUNDARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | POWERGRID | 09-05-2026 | 16:41 | KSEB | Correct Operation | R-Y PHASE FAULT, |  |  | KSEB | Correct Operation | R-Y PHASE FAULT |  |  | TRIPPED ON R-Y FAULT
168 | 400KV-MANALI-PULIYANTHOPE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 09-05-2026 | 03:51 | TANTRANSCO | Correct Operation | ZONE.1,R,N,LOCKOUT |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,LOCKOUT |  |  | Rph fault
169 | 400KV-MANALI-PULIYANTHOPE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 09-05-2026 | 03:48 | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT TRIP_Insulator decap at location: 24 |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,LOCKOUT TRIP_Insulator decap at location: 24 |  |  | bph fault
170 | 400KV/110KV MANALI-ICT-3 | TRANSFORMER | 400 | Intra | TANTRANSCO | 09-05-2026 | 22:05 | TANTRANSCO | Unwanted Operation | DC disturbance_ Shift operator Inadvertently switched OFF DC MCB | NIL | Completed | [5 empty] | DC EARTH FAULT
171 | 400KV-NCTPS_STAGE_II-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 09-05-2026 | 05:13 | TNPGCL | Correct Operation | nil |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N AR SUCCESSFUL & 3 PH TRIP |  |  | bph fault
172 | 400KV-GADAG_PSS-KUDGI_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | GTL | 08-05-2026 | 13:45 | GTL | Unwanted Operation | Direct Trip (DT) signal received from the remote end |  | Pending | PGCIL SR-2 | Unwanted Operation | Due to Manual error/ testing works by M/s Adani. | Line tripped due to DT sent by M/s Adani during Construction works. SOP to followed by Adani instructions shared with M/s Adani. | Completed | while testing of BB, Tie bay (42652) is opened
173 | 765KV-CHILAKALURIPETA-VEMAGIRI_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | PSITSL | 09-05-2026 | 13:57 | PGCIL SR-1 | Correct Operation | A/R attempted and tripped due to B-N fault in reclaim time |  |  | PGCIL SR-1 | Correct Operation | A/R attempted but tripped due to fault in reclaim time |  |  | BN fault
174 | 400KV-MANALI-PULIYANTHOPE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 09-05-2026 | 22:05 | TANTRANSCO | Unwanted Operation | DC disturbance_Shift operator inadvertently switched OFF DC MCB | NIL | Completed | TANTRANSCO | Correct Operation | DT RECEIVED |  |  | DC EARTH FAULT
175 | 400KV-ENNORE SEZ-NCTPS_STAGE_II-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 09-05-2026 | 12:13 | TNPGCL | Correct Operation | nil |  |  | TNPGCL | Correct Operation | Line fault cleared in Differential protection (within 5.0 cycle).Line patrolling is in progress. |  |  | TRIPPED DUE TO B-N LINE FAULT
176 | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 10-05-2026 | 01:44 | TGGENCO | Correct Operation | The relay tripped as per the settings. |  |  | APTRANSCO | Correct Operation | single line to ground fault |  |  | TRIPPED ON Y-N FAULT
177 | 400KV-ENNORE SEZ-SUNGAVARACHATRAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 09-05-2026 | 09:24 | TNPGCL | Correct Operation | Line fault cleared in Zone 1 (within 4.0 Cycle) |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR_INSULATOR DE-CAP AT LOC NO 43 |  |  | TRIPPED AND REASON AWAITED
178 | 400KV-GUDDIGUDEM-HINDUJA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 10-05-2026 | 16:31 | APTRANSCO | Correct Operation | feeder stood ok |  |  | HINDUJA | Correct Operation | A/R not operated due to time-based AR operation (AR Lockout occurred before re-closing due to under-voltage sensing). |  |  | TRIPPED ON B-N FAULT
179 | 400KV-GUDDIGUDEM-HINDUJA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 10-05-2026 | 16:31 | APTRANSCO | Correct Operation | AR operated and unsucceful due to persistent fault |  |  | HINDUJA | Correct Operation | A/R not operated due to time-based AR operation (AR Lockout occurred before re-closing due to under-voltage sensing). |  |  | TRIPPED DUE TO R-N FAULT
180 | 230KV-TTGS-JSW_Vilathikulam-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | JINDAL | 11-05-2026 | 09:00 | PGCIL SR-2 | Correct Operation | Due to DT recieve |  |  | JSW_RE | Correct Operation | Nil |  |  | Tripped due to tripping of ICT-2 tripping on Y-B Differential Protection
181 | 220KV-UPCL-KEMAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 09-05-2026 | 17:33 | ADANI_APL | Correct Operation | nil |  |  | KPTCL | Correct Operation | correct operation |  |  | Trip
182 | 220KV-UPCL-KEMAR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 09-05-2026 | 17:33 | ADANI_APL | Correct Operation | nil |  |  | KPTCL | Correct Operation | correct operation |  |  | Trip
183 | 400KV-ENNORE SEZ-NCTPS_STAGE_II-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 11-05-2026 | 14:07 | TNPGCL | Failure Operation | Differential Cph fault |  |  | TNPGCL | Correct Operation | nil |  |  | TRIPPED AND REASON AWAITED
184 | 400KV-VALLUR-ALAMATHY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 09-05-2026 | 08:31 | NTECL | Correct Operation | correct operation |  |  | TANTRANSCO | Correct Operation | HOLDING |  |  | Tripped
185 | 400KV-KALVENDAPATTU-VALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 09-05-2026 | 08:31 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | NTECL | Correct Operation | correct operation |  |  | CONDUCTOR SNAPPED
186 | 765KV-THIRUVALAM-ARIYALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 09-05-2026 | 13:38 | PGCIL SR-2 | Failure Operation | AR not operated @ Thiruvalam end due to CB Oil pressure Low Relclosing alarm. | The pressure settings are rectified by OEM Engineer on 11th to 13.06.2026. AR test checked ok. | Completed | TANTRANSCO | Correct Operation | ZONE.1Y,N,AR SUCCESSFUL |  |  | TRIPPED ON Y-N FAULT
187 | 220KV-RAICHUR_KA-UPPER_JURALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 09-05-2026 | 17:15 | KPTCL | Correct Operation | Main1: Tripped on DPR, Zone-1, RYB phase, L=9.188KM, Ia=148.54A, Ib=171.97A, Ic=8.225kA, 86 MTR. Main2: ripped on DPR, Zone-1, B-phase, L=9.569KM, Ia=154.084A, Ib=176.5A, Ic=8.524kA, 86 MTR, Fault duration=86.75ms. At Jurala end Main1: Tripped on DPR, Zone-1, B-phase, Fault duration=138.5ms, L=40.24KM, Fault magnitude=1.295kA. Main2: Tripped on DPR, Zone-1, Fault duration=138.5ms, L=29.04KM, Fault current Ic=965.4A. |  |  | TGGENCO | Correct Operation | Zone-1 distance protection Operated,Phase:L3-N |  |  | Tripped
188 | 220KV-MAHALINGAPURA-SAVADATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 10-05-2026 | 23:15 | KPTCL | Correct Operation | Zone-1, Y-B Phase fault |  |  | KPTCL | Correct Operation | Zone-1, B Phase, IB=1.863kA distance = 28.3km |  |  | Transient Phase to Phase fault due to heavy rain
189 | 400KV-NCTPS_STAGE_II-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 12-05-2026 | 01:42 | TNPGCL | Correct Operation | nil |  |  | TANTRANSCO | Unwanted Operation | GD stage 3 trip_shift operator inadvertently switched off the DC MCB | NIL | Completed | cooling fan cubicle trip operated
190 | 220KV-IDDUKI-KALAMASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 08-05-2026 | 13:19 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
191 | 220KV-MADAKATHARA-PALAKKAD(KL)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 08-05-2026 | 08:10 | KSEB | Correct Operation | Autoreclosed and locked out, Disc failure on line |  |  | KSEB | Correct Operation | Autoreclosed and locked out, Disc failure on line |  |  | Ann: M1 M2 DP optd, AR optd, AR L/O optd, carrier received M1:DP:A-G,Z1,59.86km,carrier received,carrier send M2:DP:A-G,Z1,59.49km,signal send, signal received
192 | 220KV-MALAPARAMBA-NALLALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 08-05-2026 | 16:56 | KSEB | Correct Operation | Both end AR lockout |  |  | KSEB | Correct Operation | Both end AR lockout |  |  | Ann: M1 M2 Diff optd, AR optd M1:Diff:R ph,Z1,31.89km M2:Diff:R ph,Z1,31.85km
193 | 220KV-IDDUKI-PALLIVASAL_EXTN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 08-05-2026 | 15:41 | KSEB | Correct Operation | AR OPERATED |  |  | KSEB | Failure Operation | PD OPERATED. | PD TIME ADJUSTED | Completed | Ann: M1 M2 DP optd M1:DP: B ph,Z1,3.936km, carrier send M2:DP: B ph,Z1,3.996km
194 | 220KV-EDAMON-KUNDARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | POWERGRID | 09-05-2026 | 16:41 | KSEB | Correct Operation | R-Y PHASE FAULT |  |  | KSEB | Correct Operation | R-Y PHASE FAULT |  |  | ANN: M2 DP optd, L/O relay optd, Carrier received M1: DP: Loop L1-L2, Z1, Carrier send, Z com, 9.8KM
195 | 220KV-EDAMON-EDAPPON-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 09-05-2026 | 16:41 | KSEB | Correct Operation | AR Operated |  |  | KSEB | Correct Operation | AR Operated |  |  | AR OPERATED
196 | 220KV-KANHIRODE-AMBALATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 09-05-2026 | 14:57 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
197 | 220KV-TALAIPARAMBA-MYLATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 09-05-2026 | 14:57 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
198 | 220KV-TALAIPARAMBA-MYLATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 10-05-2026 | 00:33 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
199 | 765KV-ARIYALUR-NCPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 11-05-2026 | 15:16 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | BREAKER OPEN STATUS |  |  | TRIPPED AND REASON AWAITED
200 | 220KV-GADAG_PSS-Vena_GadagPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | Vena_GadagPS | 12-05-2026 | 10:32 | GTL | Correct Operation | Direct Trip (DT) signal received from the remote end |  |  | Vena_GadagPS | Correct Operation | DC failure |  |  | During maintenance work, the control supply failed and the DT was sent, resulting in the tripping of the 220kV breaker
201 | 400KV-KAIGA-GUTTUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 11-05-2026 | 16:23 | NPCIL_KAIGA | Correct Operation | Fault existed for 52 ms in B phase and fault current was 2.5 kA. |  |  | KPTCL | Correct Operation | Nil |  |  | Tripped on Distance Protection, B-N fULT...90.5 km from Guttur End...Fault Current 55 Amp
202 | 400KV-GUTTUR-BTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 12-05-2026 | 16:54 | KPTCL | Correct Operation | Nil |  |  | KPCL | Correct Operation | AR was success in first attempt and due to persistent fault AR went to LOCKOUT eventually tripping all the 3 poles. |  |  | Tripped
203 | 400KV-VTPS_IV-VIJAYAWADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | ANDHRA PRADESH | 13-05-2026 | 15:08 | APGENCO | Unwanted Operation | Unwanted trip due to mal reception of DT Channel-2 from Nunna | NA (To be checked Nunna end) | Completed | PGCIL SR-1 | Correct Operation | NIL |  |  | DT received from Nunna
204 | 400KV-NARNOOR-JAMMALAMADUGU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 13-05-2026 | 17:30 | APTRANSCO | Correct Operation | Line tripped on Zcom protection. |  |  | APTRANSCO | Correct Operation | system is in order |  |  | Tripped on YB Fault(Agri fire)
205 | 400KV-NARNOOR-JAMMALAMADUGU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 13-05-2026 | 17:30 | APTRANSCO | Correct Operation | at Jammalamadugu end, line tripped on zone 5 protection. |  |  | APTRANSCO | Correct Operation | system is in order |  |  | Y-B Fault (Agri fire)
206 | 400KV-NELLORE_PG-THIRUVALAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 13-05-2026 | 20:05 | PGCIL SR-1 | Correct Operation | NIL |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | TRIPPED ON Y-N FAULT
207 | 400KV-KALVENDAPATTU-VALLUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 09-05-2026 | 08:31 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | NTECL | Correct Operation | correct operation |  |  | CONDUCTOR SNAPPED
208 | 220KV-HUBLI-NARENDRA_KP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 11-05-2026 | 13:01 | KPTCL | Correct Operation | Idle |  |  | KPTCL | Correct Operation | Zone 1, R-phase, Ia=1.45kA, distance=108.18km, TOR |  |  | Tree branches touched line b/n location No.54&55, cleared
209 | 220KV-Renew_Surya_Ojas_Koppal_W-KOPPAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | RSOPL | 15-05-2026 | 05:20 | RENEW POWER PVT LTD | Correct Operation | Line to Ground Fault. |  |  | INDIGRID | Correct Operation | Fault tripping |  |  | RN fault
210 | 400KV-KAIGA-GUTTUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 14-05-2026 | 17:39 | NPCIL_KAIGA | Correct Operation | Tripped on zone protection |  |  | KPTCL | Failure Operation | Nil | AR scheme will be checked before restoration of the line | Pending | TRIPPED ON R-N FAULT
211 | 220KV-HUBLI-SIRSI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 11-05-2026 | 13:22 | KPTCL | Correct Operation | Zone 1, R-phase, Ia= 5.37kA, distance=19.80km, |  |  | KPTCL | Correct Operation | CB in H/T Condition |  |  | Transient fault suspected due to heavy wind & lightning
212 | 400KV/220KV MADAKKATHARA-ICT-1 | TRANSFORMER | 400 | Intra | KSEB | 14-05-2026 | 19:00 | KSEB | Correct Operation | NA | [7 empty] | PRV OPERATED
213 | 400KV-KAIGA-GUTTUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 14-05-2026 | 17:39 | NPCIL_KAIGA | Correct Operation | Tripped on zone protection |  |  | KPTCL | Correct Operation | Nil |  |  | TRIPPED ON B-N FAULT
214 | 220KV-KUDGI_NTPC-NANDHIHAL-4 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 13-05-2026 | 19:34 | NTPC_KUDGI | Correct Operation | As per Nadhihal Substation, Heavy Sparks observed at Bus Side Isolator at Nadhihal end, They have hand tripped the line, DT Received at Kudgi End and Line tripped |  |  | KPTCL |  |  |  |  | DT received to Kudgi end
215 | 400KV-GUDIWADA-SATTENPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 15-05-2026 | 15:38 | APTRANSCO | Correct Operation | Fault tripping in Z1 ,Y-Phase |  |  | APTRANSCO | Correct Operation | No visible fault observed |  |  | TRIPPED DUE TO Y-N FAULT
216 | 400KV-GUTTUR-HIRIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 15-05-2026 | 19:49 | KPTCL | Correct Operation | Nil |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct- AR Successful @Hiriyur end. |  |  | TRIPPED DUE TO R-N FAULT
217 | 220KV-MADAKATHARA-ELANKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 12-05-2026 | 16:03 | KSEB |  |  |  |  | KSEB | Correct Operation | AR Operated |  |  | AR OPERATED
218 | 400KV-KOZHIKODE-MADAKKATHARA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KSEB | 12-05-2026 | 16:40 | PGCIL SR-2 | Correct Operation | AR Successful both ends.- 21.2 km /5.7 kA. |  |  | KSEB | Correct Operation | AR Successful |  |  | AR Successful both ends on Rph-G Transient fault.
219 | 220KV-TALAIPARAMBA-MYLATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 12-05-2026 | 18:20 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
220 | 220KV-TALAIPARAMBA-MYLATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 12-05-2026 | 18:22 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
221 | 220KV-IDDUKI-KALAMASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 12-05-2026 | 16:49 | KSEB | Correct Operation | SOTF |  |  | KSEB | Correct Operation | SOTF |  |  | M1:ZONE 1 trip,PHASE A N/G,Carrier send,Carrier Received M2:Z1 TRIP, A ph TRIP, Active group 1 Tripped phase A ,Start phase AN, Fault location 31.85Km
222 | 220KV-IDDUKI-KALAMASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 14-05-2026 | 15:17 | KSEB | Correct Operation | AR/LO |  |  | KSEB | Correct Operation | AR/LO |  |  | PHASE A,PUTT TRIP,ZONE 1 TRIP,started phase AN,tripped phase A, Fault location-37.7km
223 | 220KV-KANHIRODE-AMBALATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 14-05-2026 | 16:32 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
224 | 220KV-THOTIAR-CHALAKUDY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 14-05-2026 | 17:36 | KSEB | Correct Operation | AR/LO |  |  | KSEB | Correct Operation |  |  |  | Ann: Diff protn optd, General trip, MT86 optd Diff:R ph,Z1,70.3km
225 | 220KV-TALAIPARAMBA-MYLATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 14-05-2026 | 16:31 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
226 | 220KV-MADAKATHARA-ELANKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 14-05-2026 | 19:00 | KSEB | Correct Operation | Insulation disc failure |  |  | KSEB | Correct Operation | Insulation disc failure |  |  | Ann: Line Diff trip, CB reclose alarm M2:DP:A-N,Z1,1.933km M1:Diff:A-G,Z1,3.3km 186A 186B optd
227 | 220KV-ALUVA-KOTHAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 15-05-2026 | 19:19 | KSEB |  |  |  |  | KSEB |  |  |  |  | MT86 optd M1:Diff:R-G,Z1,10.8km M2:Diff:R-G,---,12.65km
228 | 220KV-NAGJHERI-HUBLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 11-05-2026 | 16:39 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone-1, R-phase, Ia=3.65kA, distance=26.83km |  |  | Transient fault suspected due to heavy wind & lightning l.Line charged, stood OK.
229 | 400KV-NARNOOR-SRISAILAM_LEFT_BANK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 15-05-2026 | 16:45 | APTRANSCO | Correct Operation | Feeder tripped at srisailam end only without any relay indications |  |  | TGGENCO | Unwanted Operation | No faults and no trips found |  | Pending | Tripped without indication
230 | 220KV-THRISSUR HVDC-NALLALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 19:35 | PGCIL SR-2 | Correct Operation | Line tripped @ Nallam end only- No Tripping or fault in Line @ Thrissur HVDC end |  |  | KSEB | Unwanted Operation | End fault operated when switching 2ARNL#1 to the fault. Outage time increased since unsuccessful sync check since 15+kV difference between 220kV Nallalam bus and 2TRNL | Checked and corrected relay logic | Completed | end zone
231 | 220KV-TP SAURYA LIMITED-KOPPAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TATA | 16-05-2026 | 21:20 | TATA | Correct Operation | M1 & M2 protection Relay is isolated the fault on correct time. |  |  | INDIGRID | Correct Operation | Differential operated |  |  | Tripoped on differential protection
232 | 400KV-KOPPAL-KUDGI_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KNTL | 18-05-2026 | 15:30 | INDIGRID | Correct Operation | Fault tripping |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | Tripped
233 | 220KV-AMBEWADI-PONDA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | KPTCL | 17-05-2026 | 20:09 | KPTCL | Correct Operation | NA | [7 empty] | Y-N, Zone I, fault Distance:63.6KM, fault current:2.3KA from Ambewadi
234 | 765KV-RAICHUR_PG-SHOLAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | RSTCL | 18-05-2026 | 15:39 | PGCIL SR-1 | Unwanted Operation | NIL |  | Completed | [5 empty] | Tripped
235 | 400KV-MYSORE-KOZHIKODE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 17-05-2026 | 17:41 | PGCIL SR-2 | Correct Operation | Tripped due to Rph-Yph-G fault Detected in M-2 |  |  | PGCIL SR-2 | Correct Operation | AR Successful |  |  | Tripped
236 | 400KV-GUTTUR-BTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 18-05-2026 | 18:05 | KPTCL | Correct Operation | Nil |  |  | KPCL | Correct Operation | On 18/5/2026 @ 18:02hrs 400kv BTPS-Guttur Line tripped on Zone 1 distance protection |  |  | b-n, 4.9kA, 66km
237 | 400KV-MYSORE-KOZHIKODE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 17-05-2026 | 17:41 | PGCIL SR-2 | Correct Operation | Tripped Due to Multiple phase to Earth Fault Detected. |  |  | PGCIL SR-2 | Correct Operation | AR Successful @ Kozhikode end. |  |  | tripped on R-N Fault
238 | 400KV-NELAMANGALA-TALGUPPA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 18-05-2026 | 13:58 | KPTCL | Correct Operation | NIL |  |  | KPTCL | Correct Operation | Tripped on Distance protection Main 1 and Main 2 |  |  | TRIPPED ON B-N FAULT
239 | 400KV-MALKARAM-RAMAGUNDAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 16-05-2026 | 16:21 | TGTRANSCO | Failure Operation | AR not operated | Non operation of AR will be checked | Pending | NTPC_RSTPS | Correct Operation | Y phase to Earth fault, auto reclosure successful |  |  | TRIPPED DUE TO Y-N FAULT
240 | 220KV-GADAG_PSS-Vena_GadagPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | Vena_GadagPS | 17-05-2026 | 16:14 | GTL | Correct Operation | Fault tripping |  |  | Vena_GadagPS | Correct Operation | RN fault__Zone1 operated |  |  | tripped on R-N Fault
241 | 400KV-KUDGI_PG-NARENDRA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 18-05-2026 | 15:06 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | RN fault
242 | 400KV-KOPPAL-KUDGI_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KNTL | 18-05-2026 | 15:30 | INDIGRID | Correct Operation | Fault tripping |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | Tripped
243 | 220KV-GADAG_PSS-Green Infra_GadagPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | GADAG_II_A | 17-05-2026 | 16:16 | GTL | Correct Operation | Fault tripping |  |  | GREENINFRA | Correct Operation | nil |  |  | YB FAULT
244 | 765KV-ARIYALUR-NCPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 18-05-2026 | 23:30 | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TANTRANSCO | Correct Operation | CAT,R,Y |  |  | tripped on R-N Fault
245 | 220KV-HIRIYUR-Chitradurga-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 18-05-2026 | 19:04 | PGCIL SR-2 | Correct Operation | AR attempted and line tripped on TOR.12.2 km / 8.14 kA. |  |  | KPTCL | Correct Operation | Fault current 2.8kA, fault location 32.45km, TOR |  |  | TRIPPED ON B-N FAULT IN ZONE-1
246 | 220KV-HIRIYUR-INFOSYS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 18-05-2026 | 19:04 | PGCIL SR-2 | Correct Operation | AR Successful |  |  | KPTCL |  |  |  |  | DPR Nph Z1 AR successful at Infosys end
247 | 220KV-HIRIYUR-HIRIYUR_KAR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KARNATAKA | 18-05-2026 | 19:22 | PGCIL SR-2 | Correct Operation | AR Successful @ Hiriyur - Powergrid end. Tripped at Hiriyur KPTCL end. |  |  | KPTCL |  |  |  |  | TRIPPED ON R-N FAULT
248 | 220KV-NAGJHERI-BIDNAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 11-05-2026 | 16:59 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone 1, R-phase, IA=5.78kA, distance=31.5km, |  |  | suspected that due to heavy wind & lightning line might have been tripped.Line charged, stood OK.
249 | 220KV-ELAPULLY-MADAKATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 19-05-2026 | 05:32 | PGCIL SR-2 | Correct Operation | AR attempted and line tripped on TOR. 67.4 km / 2.1 kA |  |  | KSEB | Failure Operation | Breaker delay | Corrected | Completed | TRIPPED ON B-N FAULT ANN: DP optd, AR optd, VT fuse fail M1: DP: B-G-T, Z1, 12.82KM M2: DP: B-G-T Z1, 13.46KM , Carrier send
250 | 400KV/220KV JAMMALAMADUGU-ICT-1 | TRANSFORMER | 400 | Intra | APTRANSCO | 18-05-2026 | 18:40 | APTRANSCO | Correct Operation | trip in order | [7 empty] | MAL-OPERATION
251 | 400KV/220KV JAMMALAMADUGU-ICT-3 | TRANSFORMER | 400 | Intra | APTRANSCO | 18-05-2026 | 18:40 | APTRANSCO | Correct Operation | trip in order | [7 empty] | TRIPPED AND REASON AWAITED
252 | 400KV-NNTPP-PUDUCHERRY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 11-05-2026 | 10:05 | NLC | Correct Operation |  |  |  | PGCIL SR-2 | Correct Operation | AR Successful both ends. 28.4 km / 3.86 kA |  |  | Yph-G fault acted and AR operated at both ends sucessfully
253 | 400KV-NNTPP-PUDUCHERRY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 11-05-2026 | 10:05 | NLC | Correct Operation | AR |  |  | PGCIL SR-2 | Correct Operation | AR Successful both ends. 28.4 km / 3.86 kA |  |  | Yph-G fault acted and AR operated successfully on both ends
254 | 400KV-MAHESHWARAM_TG-SHANKARAPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 19-05-2026 | 19:02 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | bus bar protection operated at Shankarapally
255 | 220KV-KUDGI_NTPC-SAVALAGI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 18-05-2026 | 15:53 | NTPC_KUDGI | Correct Operation | Kudgi End Auto Reclosing Successful and Line remain in Charged condition |  |  | KPTCL | Unwanted Operation | Transient Fault |  |  | r-n, 2.4kA, 39.34KM
256 | 765KV-NCPS-NCTPS STG3-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 18-05-2026 | 23:30 | TANTRANSCO | Correct Operation | source failure |  |  | TNPGCL |  |  |  |  | in view of the loss evacuating NCPS-Ariyalur line-1
257 | 765KV-NCPS-NCTPS STG3-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | TANTRANSCO | 18-05-2026 | 23:30 | TANTRANSCO | Correct Operation | source failure |  |  | TNPGCL |  |  |  |  | in view of the loss evacuating NCPS-Ariyalur line-1
258 | 400KV-NIZAMABAD-SHANKARAPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | MTL | 19-05-2026 | 19:03 | PGCIL SR-1 | Correct Operation | NA |  |  | TGTRANSCO | Unwanted Operation | DT sent to other end | Rectified the PU PSL logic | Completed | bus bar protection operated at Shankarapally
259 | 400KV-VTPS_IV-SURYAPET-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 19-05-2026 | 18:27 | APGENCO | Correct Operation | Tripped on Zone-1 R Phase and AR unsuccessful due to persisted fault |  |  | TGTRANSCO | Correct Operation | Correct operation |  |  | TRIPPED AND REASON AWAITED
260 | 220KV-HIRIYUR_OSTRO-HIRIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | RENEW POWER PVT LTD | 18-05-2026 | 21:28 | OSTRO_KANNADA | Correct Operation | EFR ,R phase to ground |  |  | PGCIL SR-2 | Failure Operation | AR did not Operate due to DT receipt from Remote. | Hiriyur Line bays belongs to KPTCL- Line Diff relay logic issue already communicated to KPTCL. | Pending | tripped on R-N Fault
261 | 230KV-BAHOOR-KARAIKAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | POWERGRID | 19-05-2026 | 22:46 | PONDICHERRY | Correct Operation | Feeder tripped on Zone-I, B - N fault at sending end Bahour. A/R operated but unsuccessful due to persistent fault. |  |  | PONDICHERRY | Correct Operation | Feeder tripped on Zone-I, B - N fault at sending end Bahour. A/R operated but unsuccessful due to persistent fault. The feeder was kept idle charged from Bahour . |  |  | Zone-1 B-phase E/L fault (Earth fault)
262 | 400KV-ALAMATHY-SUNGAVARACHATRAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 19-05-2026 | 10:44 | TANTRANSCO | Correct Operation | DT RECEIVED |  |  | TANTRANSCO | Unwanted Operation | OVR trip_Inadertently set low value during setting revision | NIL | Completed | RELAY MALOPERATION
263 | 400KV-NIZAMABAD-SHANKARAPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | MTL | 19-05-2026 | 19:03 | PGCIL SR-1 | Correct Operation | NA |  |  | TGTRANSCO | Unwanted Operation | DT sent to other end | Rectified the PU PSL logic | Completed | bus bar protection operated at shankarapally
264 | 400KV-SATTENPALLY-VTPS_IV-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 19-05-2026 | 17:50 | APTRANSCO | Correct Operation | single line to ground fault |  |  | APGENCO | Correct Operation | Tripped on Zone-1 B Phase and A/R unsuccessful due to pesrsistant fault |  |  | TRIPPED AND REASON AWAITED
265 | 220KV-ASUPAKA-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 19-05-2026 | 11:20 | TGTRANSCO | Failure Operation | AR not operated | Main-1 D60 relay will be replaced | Pending | APGENCO | Correct Operation | THE 220 KV LS-ASPK FEEDER GOT AUTO RECLOSED AT LS END AND TRIPPED AT ASPK END. |  |  | TRIPPED ON Y-N FAULT
266 | 400KV-KETHIREDDYPALLY-SHANKARAPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 19-05-2026 | 19:03 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | bus bar protection operated at Shankarapally
267 | 400KV-TALARCHEVU-JAMMALAMADUGU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 20-05-2026 | 18:05 | APTRANSCO | Correct Operation | Relays are operated in order. |  |  | APTRANSCO | Failure Operation | tripping is in order | At Jammalamadugu end, for R-G fault in the line, Zone-1, R-Ph protection operated and tripped R-Ph of CB, later Y and B phases were opened due to suspected momentary open status of B-Ph CB. | Pending | R PHASE FAULT
268 | 400KV-KHAMMAM_PG-ASUPAKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 21-05-2026 | 13:36 | PGCIL SR-1 | Correct Operation | NA |  |  | TGTRANSCO | Correct Operation | Correct operation |  |  | TRIPPED ON B-N FAULT
269 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 21-05-2026 | 09:01 | APGENCO | Correct Operation | FEEDER TRIPPED DUE TO FAULT |  |  | TGGENCO | Correct Operation | Zone-1 Distance Protection operated |  |  | TRIPPED ON Y-N FAULT
270 | 132KV-WADAPALLI-PIDUGURALLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 21-05-2026 | 13:07 | TGTRANSCO | Correct Operation | idle charged from Piduguralla end, Not tripped at Wadapalli end |  |  | APTRANSCO | Correct Operation |  |  |  | Tripped b BN Fault
271 | 220KV-KURNOOL_PG_III-SAEL2-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | SAEL | 20-05-2026 | 17:26 | PGCIL SR-1 | Correct Operation | NIL |  |  | SAEL |  |  |  |  | Tripped on Y-B Fault
272 | 400KV-KARAIKUDI-PUGALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 20-05-2026 | 12:02 | PGCIL SR-2 | Correct Operation | 400KV-KARAIKUDI-PUGALUR-1 tripped at 20-05-2026 12:02 on Yph- BPh Fault. AR Not Attempt due to Ph-Ph fault |  |  | PGCIL SR-2 | Correct Operation | 400KV-KARAIKUDI-PUGALUR-1 tripped at 20-05-2026 12:02 on Yph- BPh Fault. AR Not Attempt due to Ph-Ph fault |  |  | Tripped on Y-B Fault
273 | 220KV-CHILLAKALLU-SURYAPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 20-05-2026 | 13:24 | APTRANSCO | Correct Operation | Unwanted Operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | Bph, SOTF Operated
274 | 400KV-KHAMMAM_PG-ASUPAKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 20-05-2026 | 13:45 | PGCIL SR-1 | Correct Operation | NA |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | bph fault
275 | 400KV-GUDDIGUDEM-HINDUJA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 21-05-2026 | 10:50 | APTRANSCO | Correct Operation | AR operated and unsuccessful due to persistent fault. |  |  | HINDUJA | Correct Operation | A/R Successful and tripped on persistent fault |  |  | bph fault
276 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 21-05-2026 | 13:14 | TGGENCO | Correct Operation | TRIP ABC; START A,N; 61.4KM; SOTF TOR OPTD. |  |  | APTRANSCO | Correct Operation | Tripped on Zone-1 R-phase operated |  |  | tripped on R-N Fault
277 | 220KV-RENIGUNTA-RACHAGUNNERI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 22:49 | APTRANSCO | Correct Operation | Correct operation |  |  | APTRANSCO | Unwanted Operation |  |  | Pending | Trip
278 | 220KV-RENIGUNTA-NAGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 22:49 | APTRANSCO | Failure Operation | breakdown | Failed C&R Panel replaced with new panel | Completed | APTRANSCO | Correct Operation | Correct operation |  |  | Trip
279 | 220KV-RENIGUNTA-RACHAGUNNERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 22:49 | APTRANSCO | Correct Operation | Correct Operation |  |  | APTRANSCO | Correct Operation | Correct Operation |  |  | Trip
280 | 220KV-CUDDAPAH-RENIGUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 22:49 | APTRANSCO | Unwanted Operation |  |  | Pending | APTRANSCO | Correct Operation | Correct operation |  |  | Trip
281 | 132KV-ALAMPUR-APCARBIDE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 21-05-2026 | 22:02 | TGTRANSCO | Correct Operation | Discs flashover occured at Loc No.53 |  |  | APTRANSCO | Correct Operation |  |  |  | Tripped on three phase fault
282 | 765KV-KURNOOL_PG-KURNOOL_PG_III-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | PGCIL SR-1 | 21-05-2026 | 23:40 | PGCIL SR-1 | Correct Operation | Correct operation |  |  | PGCIL SR-1 | Correct Operation | NIL |  |  | Tripped on R-B Fault
283 | 220KV-KANHIRODE-TALAIPARAMBA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:26 | KSEB | Correct Operation | SOURCE FAILURE |  |  | KSEB | Correct Operation | SOURCE FAILURE |  |  | Supply Failure
284 | 400KV-SRISAILAM_LEFT_BANK-DINDI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 21-05-2026 | 19:27 | TGGENCO | Correct Operation | The relay tripped as per the settings. |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED AND REASON AWAITED
285 | 220KV-AREACODE-VADAKARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 15-05-2026 | 23:24 | KSEB | Correct Operation | auto reclosed and lockout, actual faul, composite insulator failure |  |  | KSEB | Correct Operation | auto reclosed and lockout, composite insulator failure |  |  | Ann: DP optd, AR L/O optd M1:DP:C-G,Z1,49.486km M2:DP:C-G,Z1,60.3km
286 | 400KV/220KV GOOTY-ICT-1 | TRANSFORMER | 400 | Intra | PGCIL SR-1 | 22-05-2026 | 07:38 | PGCIL SR-1 | Correct Operation | NIL | [7 empty] | 220kV Gooty_AP Bus bar protection operated due to conductor snapping.
287 | 400KV/220KV GOOTY-ICT-2 | TRANSFORMER | 400 | Intra | PGCIL SR-1 | 22-05-2026 | 07:38 | PGCIL SR-1 | Correct Operation | NIL | [7 empty] | 220kV Gooty_AP Bus bar protection operated for Bus2 due to conductor snapping
288 | 220KV-KANHIRODE-TALAIPARAMBA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:45 | KSEB | Correct Operation | source failure |  |  | KSEB | Correct Operation | source failure |  |  | Supply Failure
289 | 220KV-AREACODE-KANHIRODE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:26 | KSEB | Correct Operation | AR OPERATED |  |  | KSEB | Correct Operation | AR NOT OPERATED, phase to phase fault check synch voltage was not availabel at Kanhirode. |  |  | Ann: M1 DP & M2 DP optd, Carrier fail M1: DP: RB, Z1, 61.3km M2: DP: CA-G, Z1, 64.73km
290 | 400KV-NELAMANGALA-HASSAN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 21-05-2026 | 19:12 | KPTCL | Correct Operation | NIL |  |  | PGCIL SR-2 | Correct Operation | line tripped On 3 phase fault as carrier aid trip |  |  | tripped and details awaited
291 | 400KV-YADADRI TPP-DINDI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 21-05-2026 | 19:27 | TGGENCO | Correct Operation | LG fault on Line |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON B-N FAULT
292 | 400KV-YADADRI TPP-DINDI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 21-05-2026 | 19:27 | TGGENCO | Correct Operation | LG fault observed on Line |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON R-N FAULT
293 | 220KV-AREACODE-KUNAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 17:58 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | AR attempted, fault persisted AR gone to lockout |  |  | Ann: M1 Diff & M2 Diff optd M1; Diff; B, 18.13km M2: Diff: B
294 | 220KV-HASSAN-GOPALPURA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 23-05-2026 | 06:46 | PGCIL SR-2 | Correct Operation | Line tripped due to R-Y ph to ph fault in line. 28.9 km/ Ir= 5.56 kA & Iy- 4.8 kA |  |  | KPTCL |  |  |  |  | Line tripped on Rph - Yph Fault .
295 | 765KV-KURNOOL_PG-CUDDAPAH-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | POWERGRID | 23-05-2026 | 01:28 | PGCIL SR-1 | Correct Operation | NA |  |  | PGCIL SR-1 | Correct Operation | NA |  |  | TRIPPED ON OVER VOLTAGE.
296 | 220KV-AREACODE-NALLALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 17:58 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | There was a conductor of an unused line snapped and felt on this feeder |  |  | There was a conductor of an unused line snapped and felt on this line
297 | 220KV-AREACODE-NALLALAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:35 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | Lightning |  |  | Ann: M1 Diff & M2 Diff optd M1; Diff; RY, ----, ----- M2: Diff: RY, ----, 27.60km
298 | 765KV-CUDDAPAH-THIRUVALAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | POWERGRID | 22-05-2026 | 02:15 | PGCIL SR-1 | Correct Operation | Correct operation |  |  | PGCIL SR-2 | Correct Operation | DT received at Thiruvalam SS |  |  | Tripped on Over Voltage
299 | 220KV-AREACODE-ORKKATTERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:26 | KSEB | Correct Operation | AR opertaed at Areacode end |  |  | KSEB | Correct Operation | phase to phase fault, Check Synch voltage was not availabe due to tripping of ARKH feeder |  |  | Ann: M1 DP & M2 DP optd M1: DP: ABC-G, Z1, Signal send , Signal received fault, 51.03km M2: DP: CA-G, ----, -----
300 | 400KV-BHOOPALAPALLY-WARANGAL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 22-05-2026 | 13:55 | TGGENCO | Correct Operation | Warangal-2 feeder tripped on single line to ground fault Protection. |  |  | PGCIL SR-1 | Correct Operation | NIL |  |  | tripped on R-N Fault
301 | 220KV-AREACODE-KUNAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:35 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
302 | 220KV-TALAIPARAMBA-MYLATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:26 | KSEB | Correct Operation | source failure |  |  | KSEB | Correct Operation | source failure |  |  | Source failure
303 | 220KV-AREACODE-ORKKATTERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 21:45 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
304 | 220KV-KANHIRODE-ORKKATTERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:45 | KSEB | Unwanted Operation | Main1 ZIV relay tripped during system disturbance and lightning | setting revised in ZIV relay | Completed | KSEB | Correct Operation | no tripping at receiving end |  |  | Ann: M1 DP optd, CB fault discrepency trip M1: DP: R, Z1, 355.33km
305 | 220KV-TALAIPARAMBA-MYLATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:45 | KSEB | Correct Operation | source failure |  |  | KSEB | Correct Operation | source failure |  |  | Source failure
306 | 220KV-KANHIRODE-THALASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:26 | KSEB | Correct Operation | SOURCE FAILURE |  |  | KSEB | Correct Operation | SOURCE FAILURE |  |  | Source failure
307 | 220KV-KANHIRODE-AMBALATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:26 | KSEB | Correct Operation | SOURCE FAILURE |  |  | KSEB | Correct Operation | SOURCE FAILURE |  |  | Source Failure
308 | 220KV-KANIYAMPETTA-KUNAMANGALAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 17:49 | KSEB | Correct Operation | AR Successful |  |  | KSEB | Correct Operation | AR Successful |  |  | AR OPERATED
309 | 220KV-MYLATTI-AMBALATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:26 | KSEB | Correct Operation | SOURCE FAILURE |  |  | KSEB | Correct Operation | SOURCE FAILURE |  |  | Source Failure
310 | 220KV-SRISAILAM_RIGHT_BANK-DINDI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 22-05-2026 | 12:46 | APGENCO | Correct Operation | 220KV SRISAILAM - DINDI FEEDER TRIPPED ON DISTANCE PROTECTION Y & B PHASES TRIPPED BOTH ENDS.86 A OPERATED DIRECT EARTH FAULT OPERATED |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | Tripped on Y-B Fault
311 | 220KV-SRISAILAM_RIGHT_BANK-DINDI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 22-05-2026 | 11:02 | APGENCO | Correct Operation | 220KV SRISAILAM - DINDI FEEDER TRIPPED ON DISTANCE PROTECTION Y & B PHASES TRIPPED BOTH ENDS.86 A & 86 B OPERATED |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | Tripped on Y-B Fault
312 | 400KV-GAZUWAKA-KALPAKKA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 22-05-2026 | 21:04 | PGCIL SR-1 | Correct Operation | NA |  |  | APTRANSCO | Correct Operation | line tripped on fault in dead time |  |  | Tripped due to OPGW snapping
313 | 220KV-MYLATTI-AMBALATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:45 | KSEB | Correct Operation | source failure |  |  | KSEB | Correct Operation | source failure |  |  | Source Failure
314 | 220KV-AREACODE-ORKKATTERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 18-05-2026 | 02:06 | KSEB | Correct Operation | CB reclosed and lockout, disc failure |  |  | KSEB | Correct Operation | CB reclosed and lock out, disc failure |  |  | Ann: M1 DP & M2 DP optd, AR L/O optd, CB reclosed M1: DP: C-G, Z1, 51.54km M2: DP: C-G, Z1, 51.25km
315 | 220KV-IDDUKI-PALLIVASAL_EXTN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 21-05-2026 | 15:24 | KSEB | Correct Operation | MULTI PHASE FAULT |  |  | KSEB | Correct Operation | MULTI PHASE FAULT |  |  | M1: phase ABC, zone 1 trip, AR lock out M2:PHASE R FAULT,PHASE B FAULT,start phase CAN,Fault location-7.899km Relay Indications :86A,86B,86LO
316 | 220KV-AREACODE-ORKKATTERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 22-05-2026 | 02:49 | KSEB | Correct Operation | CB Reclosed and lockout, conductor snapping |  |  | KSEB | Correct Operation | CB reclosed and lockout |  |  | ANN: M1 DP & M2 DP optd, AR L/O, CB Re closed M1: DP: C-G, Z1, 32.52KM M2: DP: C-G, Z1, 32.25KM
317 | 220KV-KANHIRODE-THALASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 22-05-2026 | 03:01 | KSEB | Unwanted Operation |  | trip bus configuration in L-90 relay modified | Completed | KSEB | Correct Operation | No tripping at receiving end |  |  | ANN: M2 DP optd, AR optd M2: DP: No indications
318 | 220KV-AMBALAMUGAL-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 22-05-2026 | 05:10 | KSEB |  |  |  |  | KSEB | Correct Operation | AR OPTD |  |  | AR OPERATED
319 | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 23-05-2026 | 16:34 | APTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | Idle charged from Peddagopathi end. hence not tripped at Chillakallu end |  |  | B-N, 24.5 Kms, 3.01 kA
320 | 400KV-TELANGANA_STPP-RAMADUGU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 24-05-2026 | 13:30 | NTPC_TESTPP | Correct Operation | line auto erlcosed was succesful. busreactor operated as per the setting |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED DUE TO R-N FAULT
321 | 400KV-GUDDIGUDEM-HINDUJA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 23-05-2026 | 15:25 | APTRANSCO | Correct Operation | SINGLE PHASE TO GROUND FAULT ON Bphase. AR unsccessful due to Persistent fault. |  |  | HINDUJA | Correct Operation | A/R not operated due to time-based AR operation (AR Lockout occurred before re-closing due to under-voltage sensing). |  |  | HIN: B-N, Z-1, 57.8 Kms, 5.8 kA; GUD: B-N, Z-1, 2.5 kA, 130 Kms
322 | 132KV-ALAMPUR-APCARBIDE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 23-05-2026 | 18:20 | TGTRANSCO | Correct Operation | idle charged from Alampur end, Not tripped at Kurnool end |  |  | APTRANSCO | Correct Operation |  |  |  | Tripped on B-N fault. 2.3kA
323 | 220KV-NAGJHERI-HUBLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 12-05-2026 | 16:06 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone 1, Y-phase, Ib=7.0kA, distance=8.938kms, |  |  | Transient fault, AR Successful at Hubli end
324 | 132KV-ALAMPUR-APCARBIDE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 23-05-2026 | 18:20 | TGTRANSCO | Correct Operation | idle charged from Alampur end, Not tripped at Kurnool end |  |  | APTRANSCO | Correct Operation |  |  |  | Tripped on B-N fault. 2.3kA
325 | 400KV-NAGARJUNASAGAR_PG-RAMAGUNDAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 23-05-2026 | 13:41 | PGCIL SR-1 | Correct Operation | Nil |  |  | NTPC_RSTPS | Correct Operation | correct operation |  |  | TRIPPED DUE TO R-N FAULT
326 | 400KV-SATTENPALLY-VTPS_IV-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 24-05-2026 | 19:02 | APTRANSCO | Correct Operation | Distance protection operated |  |  | APGENCO | Correct Operation | Tipped as per logic |  |  | bph fault
327 | 400KV-SIMHADRI-VEMAGIRI_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 23-05-2026 | 15:21 | NTPC_SIMHADRI | Correct Operation | correct operation |  |  | APTRANSCO | Correct Operation | Single phase to ground fault on the line. AR unsuccessful due to persistent fault. |  |  | TRIPPED DUE TO B-N LINE FAULT
328 | 400KV-YEDULA-VATTEM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 24-05-2026 | 03:19 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | Tripped on Over Voltage
329 | 400KV-JINDAL-BPS-4 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 23-05-2026 | 22:38 | JSW_THERMAL | Unwanted Operation | due GPR issue |  | Pending | KPTCL | Correct Operation |  |  |  | Tripped at JSW end, No abnormalities
330 | 400KV-GADAG_PSS-KOPPAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | GADAG_II_A | 23-05-2026 | 18:13 | GTL | Correct Operation | Fault Tripping |  |  | INDIGRID | Correct Operation | Fault tripping |  |  | Y-B fault due to Tower collapse at Location number at AP 11/5 and AP 11/6
331 | 400KV-GADAG_PSS-KOPPAL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | GADAG_II_A | 23-05-2026 | 18:13 | GTL | Correct Operation | Fault tripping |  |  | INDIGRID | Correct Operation | Fault tripping |  |  | Y-B fault due to Tower collapse at Location number at AP 11/5 and AP 11/6
332 | 400KV-KUDGI_PG-KHOLAPUR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 24-05-2026 | 00:23 | PGCIL SR-2 | Correct Operation | Line tripped on R -G fault. AR attempted but tripped due to persistant fault | [7 empty] | TRIPPED ON R-N FAULT
333 | 400KV/220KV GUTTUR-ICT-2 | TRANSFORMER | 400 | Intra | KPTCL | 25-05-2026 | 02:15 | KPTCL | Correct Operation | Nil | [7 empty] | Differential relay operated
334 | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 25-05-2026 | 13:38 | APTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation |  |  |  | Tripped on Y-B Fault
335 | 220KV-WARANGAL-HUZURABAD-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 25-05-2026 | 14:51 | PGCIL SR-1 | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | Earth wire snapped between loc Nos 91 to 93 |  |  | YB fault
336 | 230KV-TTGS-Ettayapuram-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | NTPC | 24-05-2026 | 13:21 | PGCIL SR-2 | Correct Operation | Line tripped on B-G fault and further DT Received from the remote end in the dead time |  |  | NTPC |  |  |  |  | TRIPPED DUE TO B-N LINE FAULT
337 | 400KV-UDUMALPET_PG-PUGALUR HVDC-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 24-05-2026 | 22:42 | PGCIL SR-2 | Correct Operation | AR attempted but tripped due to persistant fault. |  |  | PGCIL SR-2 | Correct Operation | Auto reclosure was attempted and line tripped due to persistant fault. |  |  | TRIPPED ON R-N FAULT
338 | 400KV-JINDAL-BPS-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KPTCL | 23-05-2026 | 22:38 | JSW_THERMAL | Unwanted Operation | due to GPR issue |  | Pending | KPTCL | Correct Operation |  |  |  | Tripped at JSW end, No abnormalities
339 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 24-05-2026 | 10:44 | TGGENCO | Correct Operation | Tripped at KTPS end and No indications found in relay |  |  | APTRANSCO | Correct Operation | Not tripped at Tiruvuru end |  |  | TRIPPED ON R-N FAULT
340 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 24-05-2026 | 15:27 | TGGENCO | Correct Operation | Trip A,N; zone-1; 19.17KM; AR Lockout optd |  |  | APTRANSCO | Correct Operation | Not tripped at Tiruvuru end and Tripped at KTPS end |  |  | A/R successful from Tiruvuru end. R-ph, 1.14 KA, 77.7km from Tiruvuru end.
341 | 400KV-GAJWEL-RAMAGUNDAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 24-05-2026 | 16:09 | TGTRANSCO | Failure Operation | AR not operated |  |  | NTPC_RSTPS | Correct Operation | correct operation |  |  | Tripped. A/R successful from Ramagundam end
342 | 400KV-JULURUPADU-MANUGURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 24-05-2026 | 15:43 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGGENCO | Correct Operation | AR operated and aborted due to trip again during reclaim time. |  |  | Tripped on B-ph fault. 17.6 KM, 10.4 KA from Julurupadu end
343 | 400KV-GAJWEL-RAMAGUNDAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 24-05-2026 | 13:20 | TGTRANSCO | Failure Operation | AR not operated | Non operation of AR will be checked | Pending | NTPC_RSTPS | Correct Operation | correct operation |  |  | TRIPPED ON Y-N FAULT
344 | 765KV-WARANGAL(NEW)-CHILAKALURIPETA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | WKTL | 25-05-2026 | 16:53 | ADANI_ATL | Correct Operation | Zone-1 |  |  | PGCIL SR-1 | Correct Operation | Tripped on B Ph fault |  |  | Tripped on B phase fault 3.57kA
345 | 765KV-WARANGAL(NEW)-CHILAKALURIPETA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | WKTL | 25-05-2026 | 16:53 | ADANI_ATL | Correct Operation | B-G fault |  |  | PGCIL SR-1 | Correct Operation | A/R operated and tripped on persisting fault |  |  | TRIPPED ON B-N FAULT
346 | 220KV-CHITTOOR-RENIGUNTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 22:49 | APTRANSCO | Correct Operation | Operation is in proper order |  |  | APTRANSCO | Correct Operation | Correct operation |  |  | Trip
347 | 220KV-ASUPAKA-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 26-05-2026 | 00:12 | TGTRANSCO | Correct Operation | Correcet operation |  |  | APGENCO | Unwanted Operation | Due to detection of BRC , both the feeders hand tripped at LS end |  | Pending | Tripped due to Bus bar protection on 220 KV Lower Sileru Bus-2
348 | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 26-05-2026 | 23:51 | APTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | Idle charged from Peddagopathiend. hence not tripped at Chillakallu end |  |  | tripped on yb fault zone-2
349 | 765KV-WARANGAL(NEW)-WARORA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | WKTL | 25-05-2026 | 14:51 | ADANI_ATL | Correct Operation | Zone-1 | [7 empty] | Tripped on R-B Fault
350 | 132KV-WADAPALLI-PIDUGURALLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 25-05-2026 | 17:18 | TGTRANSCO | Correct Operation | idle charged from Piduguralla end, Not tripped at Wadapally end |  |  | APTRANSCO | Correct Operation |  |  |  | tripped on B-G fault
351 | 400KV/220KV GAJWEL-ICT-1 | TRANSFORMER | 400 | Intra | TGTRANSCO | 27-05-2026 | 06:02 | TGTRANSCO | Correct Operation | Correcet operation | [7 empty] | Tripped alongwith GAJWEL - 400KV - Bus 1
352 | 220KV-VTPS-RENTACHINTHALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-05-2026 | 17:08 | APGENCO | Correct Operation | Protection acted as per the scheme. |  |  | APTRANSCO | Correct Operation | rentachintala end operation ok |  |  | Trip
353 | 220KV-NAGJHERI-BIDNAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 12-05-2026 | 18:41 | KPCL |  |  |  |  | KPTCL | Correct Operation | Zone-1, R-Phase, Ia=4.8kA, distance=33.34km, TOR |  |  | Transient fault
354 | 220KV-CHILLAKALLU-PULICHINTALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 26-05-2026 | 23:51 | APTRANSCO | Correct Operation | abnormal weather condition |  |  | TGGENCO | Correct Operation | Fault tripping |  |  | tripped on RY fault
355 | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 26-05-2026 | 20:59 | APTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | Idle charged from Peddagopathi end. Hence not tripped at Chillakallu end |  |  | R-N Fault Zone-1 29km 2.9kA
356 | 220KV-AREACODE-KANHIRODE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:28 | KSEB | Correct Operation | AR Operated at Areacode |  |  | KSEB | Correct Operation | AR Not operated, Check Synch voltage was not available at Kanhirode, as 2AROR also tripped |  |  | Trip
357 | 400KV-ILFS-NAGAPATTNAM_PS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | ILFS | 22-05-2026 | 12:45 | ILFS | Correct Operation | Zone 2 operated & Carrier not received |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. AR successful |  |  | Trip
358 | 132KV-BONAKAL-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 27-05-2026 | 00:01 | TGTRANSCO |  |  |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON B-N FAULT
359 | 132KV-BONAKAL-CHILLAKALLU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | TGTRANSCO | 26-05-2026 | 23:53 | TGTRANSCO |  |  |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON B-N FAULT
360 | 400KV-GHANAPUR-GAJWEL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 27-05-2026 | 06:02 | PGCIL SR-1 | Correct Operation | Line tripped only at Gajwel end and holding from Ghanapur end. As per information received from Gajwel, line tripped at their end due to tripping of 400kV Bus 1, ICT-1&2 at Gajwel SS. |  |  | TGTRANSCO | Unwanted Operation | spurious tripping |  |  | Tripped alongwith GAJWEL - 400KV - Bus 1
361 | 220KV-AREACODE-ORKKATTERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 17-05-2026 | 18:28 | KSEB | Correct Operation | AR Operated at Areacode |  |  | KSEB | Correct Operation | AR Not operated, 2ARKH tripped from Kanhirode, Check synch voltage was not available at Orkattery |  |  | Trip
362 | 400KV-NIRMAL-SUNDILA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 26-05-2026 | 20:49 | TGTRANSCO | Failure Operation | AR not operated |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON B-N FAULT
363 | 765KV-KURNOOL_PG-MAHESHWARAM_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | POWERGRID | 26-05-2026 | 18:59 | PGCIL SR-1 | Correct Operation | NA |  |  | PGCIL SR-1 | Correct Operation | NA |  |  | TRIPPED AND REASON AWAITED
364 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 25-05-2026 | 13:54 | TGGENCO | Correct Operation | TRIP B,N;Z2;79.83KM; AR LOCKOUT OPTD |  |  | APTRANSCO | Correct Operation | Tripped on Zone-1 Y and B phase operated |  |  | Tripped on Y-B Fault
365 | 765KV-CHILAKALURIPETA-VEMAGIRI_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Intra | PSITSL | 26-05-2026 | 23:30 | PGCIL SR-1 | Correct Operation | L-L Fault |  |  | PGCIL SR-1 | Correct Operation | LL fault |  |  | RB fault
366 | 400KV-HASSAN-HEBBANAHALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KARNATAKA | 27-05-2026 | 13:26 | PGCIL SR-2 | Correct Operation | 400KV-HASSAN-HEBBANAHALLI-1 tripped at 27-05-2026 13:26. AR attempted but unsuccessful due to persisting fault. |  |  | KPTCL | Correct Operation | Tripped on Zone-1, L2 - N |  |  | TRIPPED ON Y-N FAULT
367 | 400KV-RAMADUGU-GAJWEL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 26-05-2026 | 21:54 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED ON B-N FAULT
368 | 400KV/220KV GAJWEL-ICT-2 | TRANSFORMER | 400 | Intra | TGTRANSCO | 27-05-2026 | 06:02 | TGTRANSCO | Correct Operation | Correcet operation | [7 empty] | Tripped alongwith GAJWEL - 400KV - Bus 1
369 | 400KV-GAJWEL-CHANDALAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 26-05-2026 | 21:40 | TGTRANSCO | Unwanted Operation | spurious tripping |  |  | TGTRANSCO | Correct Operation | Line is in service at Chandulapur end |  |  | RYB FAULT
370 | 400KV-RAMADUGU-GAJWEL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 26-05-2026 | 21:40 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | tripped on R-N Fault
371 | 400KV-CHOUTUPPAL-KHAMMAM_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 26-05-2026 | 19:42 | TGTRANSCO | Correct Operation | Correcet operation |  |  | PGCIL SR-1 | Correct Operation | NA |  |  | Choutuppal: R-N, 18.4km, 8.90kA
372 | 765KV-WARANGAL(NEW)-CHILAKALURIPETA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | WKTL | 26-05-2026 | 23:50 | ADANI_ATL | Correct Operation | line tripped due to bad weather |  |  | PGCIL SR-1 | Failure Operation | Tripped on R-N fault |  | Completed | Tripped
373 | 400KV-GAJWEL-RAMAGUNDAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 27-05-2026 | 06:02 | TGTRANSCO | Unwanted Operation | spurious tripping |  |  | NTPC_RSTPS | Correct Operation | correct operation |  |  | Tripped alongwith GAJWEL - 400KV - Bus 1
374 | 400KV-DICHPALLY-NIRMAL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 27-05-2026 | 00:41 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | R-ph LA blast at Nirmal end
375 | 220KV-NAGJHERI-BIDNAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 16-05-2026 | 20:16 | KPCL |  |  |  |  | KPTCL |  | Zone 1, R-phase, IA=6.45kA, distance=29.336km |  |  | Transient fault
376 | 400KV-GAJWEL-NARSAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 26-05-2026 | 21:40 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Failure Operation | AR not operated |  |  | RYB FAULT
377 | 220KV-HIRIYUR-Chitradurga-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 27-05-2026 | 22:55 | PGCIL SR-2 | Correct Operation | AR attempted and tripped on TOR. 41.6 km, 3.66 kA. |  |  | KPTCL | Correct Operation | RN fault, 10.97kA,2.58km, AR block due to close fault |  |  | TRIPPED ON R-N FAULT, jumper cut in Tower loc 8.
378 | 220KV-LOWER PERIYAR-MADAKATHARA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 24-05-2026 | 08:10 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
379 | 765KV-KURNOOL_PG_III-MAHESHWARAM_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | PGCIL SR-1 | 29-05-2026 | 03:23 | PGCIL SR-1 | Correct Operation | A/R successful on R-ph fault. Line tripped on 2nd fault 5 sec after successful A/R |  |  | PGCIL SR-1 | Correct Operation | A/R successful on R-ph fault. Line tripped on 2nd fault 5 sec after successful A/R |  |  | TRIPPED DUE TO R-N FAULT
380 | 220KV-IDDUKI-KALAMASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 23-05-2026 | 16:00 | KSEB | Correct Operation | MULTI PHASE FAULT |  |  | KSEB | Correct Operation |  |  |  | M1:ZONE 1 trip,PHASE A, PHASE C,N/G,Carrier send,Carrier Received,AR lockout M2:Z1 TRIP,Distance trip Z1, Active group 1, Tripped phase ABC ,Start phase ACN, Fault location=8.192Km Relay Indications : Zone 1,86LO
381 | 400KV-KAMUDHI-OTTAPIDARAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 28-05-2026 | 16:34 | TANTRANSCO | Failure Operation | ZONE.1R,N,LOCKOUT | AR SCHEME HAS TO BE CHECKED | Pending | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | Rph fault
382 | 400KV-KALVENDAPATTU-VALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 28-05-2026 | 06:15 | PGCIL SR-2 | Correct Operation | Fault in Vallur jurisdiction. Wave trap failed at Vallur end. |  |  | NTECL | Correct Operation | LINE TRIP DURING FAULT |  |  | TRIPPED ON Y-N FAULT
383 | 220KV-IDDUKI-KALAMASSERY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 23-05-2026 | 16:00 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
384 | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | TGTRANSCO | 28-05-2026 | 18:18 | TGGENCO | Correct Operation | The relay tripped as per the settings. |  |  | APTRANSCO | Correct Operation | feeder tripped on Distance protection operated and single line to ground fault |  |  | TRIPPED AND REASON AWAITED
385 | 400KV-OTTAPIDARAM-THENNAMPATTY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 28-05-2026 | 15:40 | TANTRANSCO | Failure Operation | ZONE.1,Y,N, LOCKOUT | M2 Relay Issued 3pole trip after 30 msec. AR scheme checked in next Lc. | Pending | TANTRANSCO | Failure Operation | ZONE.1,Y,N _ relay sensed the fault in Y phase but breaker open in R phase due to scheme wiring issue. Hence non clearance of fault observed at Thennampatty end. | At THENNAMPATTY SS, the breaker & relays in 400kV Ottapidaram-2 # were tested on 29.05.2026. It was observed that in the 400kV Breaker Marshalling box, the R & Y phase cables ( both tripping & status wires) were interchanged due to ferruling mix up. The wiring were set right, the breaker single pole trip from both Main-1 & Main-2 relays were checked and operation of the correct breaker pole for each trip was ensured. The operation of Auto-reclosure & LBB functions were also tested and found to be in order. The DR from the Main-1 & Main-2 were transplayed from relay testing kit in respective relays & vice versa. Both Main-1 & Main-2 operated exactly as during the fault . | Completed | Reason awaited
386 | 220KV-IDDUKI-KALAMASSERY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 23-05-2026 | 14:42 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
387 | 400KV-KAYATHAR-KANARPATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 28-05-2026 | 15:40 | TANTRANSCO | Correct Operation | Holding at Kayathar end |  |  | TANTRANSCO | Correct Operation | ZONE.3,Y,N_Due to non clearence of fault in 400kV Ottapidaram_Thennampaaty line fault at Thennampatty end, Kanarpatty end clear the fault in Zone.3 |  |  | TRIPPED AND REASON AWAITED
388 | 400KV-VEMAGIRI_AP-KV_KOTA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 28-05-2026 | 20:05 | APTRANSCO | Correct Operation | Feeder tripped on distance protection operated at Vemagiri end for Zone-1, Y-ph to ground fault on the line and AR successful. But fault resurfaced within reclaim time and 3-Ph tripping occurred. |  |  | APTRANSCO | Correct Operation | Zone 1 y phase to ground fault. |  |  | Vemagiri: Y-N, 7kA, 40.35KM
389 | 220KV-EDAMON-POTHENCODE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 23-05-2026 | 05:38 | KSEB | Correct Operation | AR Operated |  |  | KSEB | Correct Operation | correct operation |  |  | AR OPERATED,Z1 FAULT
390 | 400KV-KAYATHAR-KANARPATTI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 28-05-2026 | 15:40 | TANTRANSCO | Correct Operation | Holding at Kayathar end |  |  | TANTRANSCO | Correct Operation | ZONE.3,Y,N_Due to non clearence of fault in 400kV Ottapidaram_Thennampaaty line fault at Thennampatty end, Kanarpatty end clear the fault in Zone.3 |  |  | TRIPPED AND REASON AWAITED
391 | 400KV-KAYATHAR-THENNAMPATTY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TANTRANSCO | 28-05-2026 | 15:40 | TANTRANSCO | Correct Operation | Y, G, Zone-3_Due to non clearence of fault in 400kV Ottapidaram_Thennampaaty line fault at Thennampatty end, Kayathar end clear the fault in Zone.3 |  |  | TANTRANSCO | Correct Operation | Holding at Thennampatty end. |  |  | TRIPPED AND REASON AWAITED
392 | 220KV-BRAHMPURAM-LOWER PERIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 23-05-2026 | 15:24 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | Ann: M1 M2 DP optd, AR optd M1:DP:Bph,Z1,---- M2:DP:Bph,Z1,----, CARRIER receive and send
393 | 220KV-BRAHMPURAM-LOWER PERIYAR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 23-05-2026 | 15:24 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
394 | 400KV-TIRUNELVELI-KOTTAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 23-05-2026 | 17:13 | PGCIL SR-2 | Correct Operation | AR Successful both ends. 177.1 km/ 2.78 kA |  |  | KSEB | Correct Operation | AR |  |  | AR Successful both ends on Yph-G Transient Fault.
395 | 220KV-SABARIGIRI-PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 25-05-2026 | 18:28 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | Trip initated from the control kisosk at yard (trouble in the contacts of emergency push button in the control kiosk at yard and rectified the defect)
396 | 220KV-Pallivasal-PALLIVASAL_EXTN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 23-05-2026 | 17:31 | KSEB | Correct Operation | DISC FLASH |  |  | KSEB | Correct Operation | DISC FLASH |  |  | Ann: M1 M2 Diff protn optd M1:Diff: Y ph,---,0.5km M2:Diff: Y ph,Z2-Z3,69m
397 | 220KV-THOTIAR-CHALAKUDY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 24-05-2026 | 08:10 | KSEB | Correct Operation | AR/LO |  |  | KSEB | Failure Operation | Communication failure | High loss | Pending | Ann: M1 Diff protn optd, Z1 trip M1: Diff: B-N, Z1, 54.1km
398 | 220KV-LOWER PERIYAR-IDDUKI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 24-05-2026 | 20:48 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
399 | 220KV-KANHIRODE-TALAIPARAMBA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 26-05-2026 | 12:47 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
400 | 220KV-SABARIGIRI-PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 27-05-2026 | 19:17 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
401 | 220KV-EDAMON-EDAPPON-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 27-05-2026 | 20:17 | KSEB | Correct Operation | AR Operated |  |  | KSEB | Correct Operation | AR Operated |  |  | AR OPERATED,Z1 FAULT
402 | 220KV-BRAHMPURAM-LOWER PERIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 27-05-2026 | 12:19 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
403 | 400KV-THALLAYAPALEM-SATTENPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 28-05-2026 | 22:36 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation | feeder tripped on Distance protection operated and single line to ground fault |  |  | B-N , 52.9km, 6.33kA
404 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 28-05-2026 | 14:52 | TGGENCO | Correct Operation | TRIP ABC; START C,N; 89.82KM; 2.109KA |  |  | APTRANSCO | Correct Operation | No fault line |  |  | yph fault
405 | 400KV-DICHPALLY-RAMAGUNDAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 28-05-2026 | 18:37 | TGTRANSCO | Correct Operation | Correcet operation |  |  | NTPC_RSTPS | Correct Operation | correct operation |  |  | TRIPPED AND REASON AWAITED
406 | 400KV-MYSORE-KOZHIKODE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 27-05-2026 | 15:07 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | RB phase fault
407 | 400KV-KOPPAL-KUDGI_PG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KNTL | 29-05-2026 | 14:25 | INDIGRID | Unwanted Operation | Direct Trip (DT) signal received from the remote end |  | Pending | PGCIL SR-2 | Unwanted Operation | DT sent during Bus-II SD Work by M/s Adani | Instructions for SOP to be strictly followed is communicated to M/s Adani. | Completed | Breaker Tripped at Koppal side
408 | 220KV-KOTHAMANGALAM-Pallivasal-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 27-05-2026 | 16:46 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation | DISC FLASH AT LOC.105 |  |  | Ann: M1 Diff DP & M2 Diff DP optd M1; DP: Rph, Z1, 38.20km M2: DP: Rph, Z1, 38.69km
409 | 220KV-EDAMON-POTHENCODE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-05-2026 | 12:19 | KSEB | Correct Operation | correct operation |  |  | KSEB | Correct Operation | correct operation |  |  | Ann: M1 M2 DP optd M1:DP:No indication M2:DP:R-B ph,Z1,36.66km,L3-L1,fuse fail,ZCOM
410 | 220KV-EDAMON-POTHENCODE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 28-05-2026 | 12:19 | KSEB | Correct Operation | correct operation |  |  | KSEB | Correct Operation | correct operation |  |  | Ann: M1 M2 DP optd M1:DP:R-B ph,Z1,,38.47km,L3-L1, fuse fail M2:DP:R-B ph,Z1,38.45km
411 | 400KV-HASSAN-HEBBANAHALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KARNATAKA | 30-05-2026 | 21:39 | PGCIL SR-2 | Correct Operation | 400kV Hassan-Hebbanahalli line-1 tripped on persisting fault of Yph-G at 21.39. AR attempted but tripped due to persisitant fault. |  |  | KPTCL | Correct Operation | Tripped on Zone-1, L2 - N |  |  | Y N FAULT
412 | 220KV-HASSAN-GOPALPURA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 31-05-2026 | 11:05 | PGCIL SR-2 | Correct Operation | AR successful @ Hassan(PG) end. |  |  | KPTCL |  |  |  |  | TRIPPED ON Y-N FAULT
413 | 400KV-GUDIWADA-SATTENPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 28-05-2026 | 21:25 | APTRANSCO | Correct Operation | Fault tripping in Z1 ,B-Phase |  |  | APTRANSCO | Correct Operation | single line to ground fault |  |  | TRIPPPED AND REASON AWAITED
414 | 400KV/220KV VIJAYAWADA-ICT-2 | TRANSFORMER | 400 | Intra | PGCIL SR-1 | 25-05-2026 | 11:10 | PGCIL SR-1 | Correct Operation | Tripped on through fault | [7 empty] | Trip
415 | 220KV-VIJAYAWADA-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-05-2026 | 11:10 | APTRANSCO | Correct Operation | AR successful & tripped 3 Phase on persistent fault |  |  | APTRANSCO | Correct Operation | Tripped on B-phase fault current |  |  | Trip
416 | 400KV-GUDDIGUDEM-HINDUJA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 28-05-2026 | 19:32 | APTRANSCO | Correct Operation | AR operated and unsuccessful due to persistent fault. |  |  | HINDUJA | Correct Operation | A/R not operated due to time-based AR operation (AR Lockout occurred before re-closing due to under-voltage sensing). |  |  | Rph fault
417 | 765KV-WARANGAL(NEW)-WARORA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | WKTL | 31-05-2026 | 15:55 | ADANI_ATL | Correct Operation | Tripped due to R-Phase to Y-Phase | [7 empty] | R-N fault, A/R successful at Warora end
418 | 765KV-WARANGAL(NEW)-WARORA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | WKTL | 31-05-2026 | 16:14 | ADANI_ATL | Correct Operation | Tripped due to R-Phase to Y-Phase | [7 empty] | WARORA SS: 37.1KM, Z-1, R-N, If: 12.53kA
419 | 765KV-WARANGAL(NEW)-WARORA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 765 | Inter | WKTL | 31-05-2026 | 15:55 | ADANI_ATL | Correct Operation | Tripped due to R-Phase to Y-Phase | [7 empty] | WARANGAL(NEW): Fault Distance: 352.1 KM, Zone: 2, R-Y Fault, Ir-2.816KA, Iy-3.127KA
420 | 400KV-MYSORE-KOZHIKODE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 31-05-2026 | 16:05 | PGCIL SR-2 | Correct Operation | 400kV Mysore-Kozhikode Line 1 tripped due to R Ph-B ph fault |  |  | PGCIL SR-2 | Correct Operation | 400kV Mysore-Kozhikode Line 1 tripped due to R Ph-B ph fault |  |  | Mysore: R-B, IR 2.85KA, IB= 3.156, 176KM
421 | 400KV-NAGARJUNASAGAR_PG-RAMAGUNDAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 31-05-2026 | 12:53 | PGCIL SR-1 | Correct Operation | NIL |  |  | NTPC_RSTPS | Correct Operation | correct operation |  |  | Tripped on B-N Fault RMGDM:92KM, 3.2KA
422 | 220KV-KOTTAYAM-PALLOM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-05-2026 | 23:06 | KSEB | Correct Operation | AR |  |  | KSEB | Correct Operation | AR |  |  | AR OPERATED
423 | 220KV-BRAHMPURAM-INFO_PARK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 22-05-2026 | 05:10 | KSEB |  |  |  |  | KSEB |  |  |  |  | ANN: M1 Diff prot optd , M2 Diff prot optd, 87L optd M1: Diff: A-N, Z1, 81.54mtr M2: Diff: R Ph, - CT Flashed
424 | 400KV-KHAMMAM_PG-NAGARJUNASAGAR_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 29-05-2026 | 17:14 | PGCIL SR-1 | Correct Operation | NIL |  |  | PGCIL SR-1 | Unwanted Operation |  |  | Completed | Tripped due to relay mal operation during relay testing
425 | 220KV-SHIRALKOPPA-SHARAVATHY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 17-05-2026 | 01:32 | KPTCL | Correct Operation | YB fault in ZOne-1 at Sharavathy end |  |  | KPCL |  |  |  |  | Between tower location No. 44-45 Acacia tree fallen on line.
426 | 132KV-CHILLAKALLU-PEDAGOPATHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 132 | Inter | APTRANSCO | 31-05-2026 | 15:11 | APTRANSCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | Idle charged from Peddagopathi end. Hence not tripped at Chillakallu end |  |  | TRIPPED ON B-N FAULT
427 | 400KV-RAYALSEEMA TPP-KALIKIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 30-05-2026 | 16:08 | APGENCO | Correct Operation | Zone-1,R-N fault |  |  | APTRANSCO | Correct Operation | Tripped on Zone 1 r ph trip with a distance at 164km |  |  | Rph-N Fault, 164.63kms, 2.3kA kalikiri end
428 | 220KV-Chintur-BG Kothur-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | ANDHRA PRADESH | 31-05-2026 | 23:28 | APTRANSCO | Failure Operation | fault comes under telangana |  | Pending | TGTRANSCO | Failure Operation | AR not operated |  | Pending | Tripped on R-N fault
429 | 400KV-NAGARJUNASAGAR_PG-MEHBOOBNAGAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 29-05-2026 | 17:14 | PGCIL SR-1 | Unwanted Operation | NIL |  | Completed | TGTRANSCO | Correct Operation | Correcet operation |  |  | Tripped due to relay mal operation during relay testing
430 | 400KV-NAGARJUNASAGAR_PG-RAMAGUNDAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 29-05-2026 | 17:14 | PGCIL SR-1 | Unwanted Operation | NIL |  | Completed | NTPC_RSTPS | Correct Operation | correct operation |  |  | Tripped due to relay mal operation during relay testing
431 | 220KV-KOLAR_AC-T GOLLAHALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 30-05-2026 | 14:18 | PGCIL SR-2 | Correct Operation | Line tripped due to Phase- Phase fault in line. |  |  | KPTCL | Correct Operation | No visual fault detected during line inspection |  |  | Tripped on R-Y Fault in Zone-1, At Gollahally end fault location 11.609km, fault current 3.05kA; Transient fault
432 | 220KV-PAVAGADA_PG-RYCHALU1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSPDCL | 29-05-2026 | 23:59 | PGCIL SR-2 | Correct Operation | 220KV-PAVAGADA_PG-RYCHALU1 tripped at 29-05-2026 23:59 on B-G fault |  |  | KSPDCL | Correct Operation | tripped on distance and differentail protection relay |  |  | B-PH Differential Protection Operated
433 | 400KV-NAGAPATTNAM_PS-TRICHY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 31-05-2026 | 17:04 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | Y-N fault followed by Y-B fault
434 | 400KV-GAJWEL-CHANDALAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 29-05-2026 | 11:26 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Unwanted Operation | spurious tripping |  |  | Tripped due to Battery bank 1 fail at Chandalapur
435 | 400KV-MALKARAM-SURYAPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 31-05-2026 | 18:17 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Correcet operation |  |  | TRIPPED DUE TO Y-N FAULT
436 | 220KV-GARIVIDI-BOBBILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 11:57 | APTRANSCO | Correct Operation | Not Applicable |  |  | APTRANSCO | Correct Operation | Not Applicable |  |  | Trip
437 | 220KV-AMBALAMUGAL-SABARIGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KSEB | 29-05-2026 | 23:06 | KSEB | Correct Operation |  |  |  | KSEB | Correct Operation |  |  |  | AR OPERATED
438 | 220KV-HAROHALLI-SOMANAHALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 31-05-2026 | 20:07 | KPTCL | Correct Operation | tripped on DPR as per protection schedule. |  |  | KPTCL | Correct Operation | Tripped on DPR as per tripping schedule |  |  | Trip
439 | 220KV-HAROHALLI-SOMANAHALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 31-05-2026 | 19:47 | KPTCL | Correct Operation | tripped on DPR as per protection schedule. |  |  | KPTCL | Correct Operation | Tripped on DPR as per tripping schedule |  |  | Trip
440 | 220KV-BOBBILI-MARADAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 11:57 | APTRANSCO | Correct Operation | Not Applicable |  |  | APTRANSCO | Correct Operation | already in break down |  |  | Trip
441 | 220KV-GARIVIDI-BOBBILI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 11:57 | APTRANSCO | Correct Operation | Not Applicable |  |  | APTRANSCO | Correct Operation | Not Applicable |  |  | Trip
442 | 400KV-ILFS-NAGAPATTNAM_PS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | ILFS | 22-05-2026 | 12:08 | ILFS |  |  |  |  | PGCIL SR-2 | Correct Operation | AR Successful at Nagapattinam end . Line tripped @ ILFS end only. |  |  | Phase to earth fault due to tree hit
443 | 400KV-ILFS-NAGAPATTNAM_PS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | ILFS | 22-05-2026 | 12:08 | ILFS |  |  |  |  | PGCIL SR-2 | Correct Operation | AR Successful at Nagapattinam end . Line tripped @ ILFS end only. |  |  | Phase to earth fault due to tree hit
444 | 220KV-BOBBILI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 11:57 | APTRANSCO | Failure Operation |  |  | Pending | APTRANSCO | Correct Operation | SOTF/TOR operated |  |  | Trip
445 | 220KV-GARIVIDI-MARADAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 11:57 | APTRANSCO | Correct Operation | Protection operated correctly |  |  | APTRANSCO | Correct Operation | SOTF/TOR operated |  |  | Trip
446 | 220KV-GARIVIDI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 11:57 | APTRANSCO | Failure Operation | Protection operated correctly |  | Pending | APTRANSCO | Correct Operation | SOTF/TOR operated |  |  | Trip
447 | 400KV/21KV SEPC-GT-1 | TRANSFORMER | 400 | Intra | SEPC | 28-05-2026 | 15:40 | SEPC | Unwanted Operation | GT Breaker tripped due to External fault | [7 empty] | Trip
448 | 400KV/220KV SOMANAHALLI-ICT-1 | TRANSFORMER | 400 | Intra | KPTCL | 31-05-2026 | 20:07 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. | [7 empty] | tripped on REF, Differential
449 | 400KV-NAGAPATTNAM_PS-TRICHY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 31-05-2026 | 17:04 | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | PGCIL SR-2 | Correct Operation | Protection Scheme Operated Correct. |  |  | Y-N fault followed by B-N fault
450 | 220KV-HOODY-MALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 29-05-2026 | 17:35 | KPTCL | Correct Operation | Transient fault |  |  | KPTCL | Correct Operation | Transient fault |  |  | Tripped
451 | 220KV-BIDNAL-SAVADATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 17-05-2026 | 15:39 | KPTCL | Correct Operation | Zone-1, R-phase, IA=4.97kA, distance=27.144km |  |  | KPTCL | Correct Operation | Zone-1, R-Phase, distance=26.50km, Ia=3.26kA |  |  | Transient fault. heavy wind rain. TOR due to persistent fault
452 | 220KV-JURALA-LOWER_JURALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 09-05-2026 | 04:38 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGGENCO | Correct Operation | Momentary earth fault, auto recloser success |  |  | R-phase to Ground fault
453 | 220KV-JURALA-LOWER_JURALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 20-05-2026 | 02:40 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGGENCO | Correct Operation | Momentary earth fault, auto recloser success |  |  | AR acted in Zone-1 in R-phase at Lower Jurala end
454 | 220KV-JURALA-LOWER_JURALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 24-05-2026 | 19:19 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGGENCO | Correct Operation | Momentary earth fault, auto recloser success |  |  | AR acted in Zone-1 in R-phase at Lower Jurala end
455 | 220KV-JURALA-LOWER_JURALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 28-05-2026 | 02:14 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGGENCO | Correct Operation | Momentary earth fault, auto recloser success |  |  | AR acted in Zone-1 in R-phase at Lower Jurala end
456 | 230KV-KUDANKULAM-TTPS | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 17:58 | NPCIL_KKNP | Correct Operation | R phase to earth fault |  |  | TNPGCL |  |  |  |  | ADL31 Line was tripped on Zone-1 distance protection, Fault distance: 3.12KM, Fault current: R-phase-11485A.
457 | 400KV-KUDGI_PG-KUDGI_NTPC-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | KTL | 04-05-2026 | 10:47 | PGCIL SR-2 | Unwanted Operation | Due to Manual Error. Main CB HT during Bus-1 Shutdown while Tie Cb was already open due to BR under SD. | Suitable Instructions to Operators are issued for checking the Dia. before doing operations. | Completed | NTPC_KUDGI | Correct Operation | DT Received from Remote End. |  |  | Maloperation
458 | 230KV-KAVANUR-MILAVITTAN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-05-2026 | 04:15 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
459 | 220KV-RTPS-MALAT-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 03-05-2026 | 13:09 | KPCL | Correct Operation |  |  |  | KPTCL |  |  |  |  | Instentineous Over current(IOC),Fault -Rph-G
460 | 220KV-RTPS-RAMASAMUDRA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 08-05-2026 | 11:56 | KPCL | Correct Operation |  |  |  | KPTCL |  |  |  |  | 220KV RTPS END:Zone-1, Fault loop Rph-Ground, Distance:7.44 KM ,I=12.59 KA
461 | 220KV-RTPS-RAMASAMUDRA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 24-05-2026 | 02:46 | KPCL | Correct Operation |  |  |  | KPTCL |  |  |  |  | 220KV RTPS END:Zone-1, Fault loop Bph-Ground, Distance: 23.68 KM ,I= 5.75 KA
462 | 230KV-Chekkanurani-SEMBATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-05-2026 | 15:36 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
463 | 230KV-KAYATHAR(TN)-TTPS-AUTO-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 03:32 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
464 | 230KV-THIRUVARUR-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 15:14 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,R,N,_PD OPERATED | AR Close pulse output contact defect in sifang relay. New output card arranged. Line clear awaited | Pending | TRANSIENT FAULT
465 | 230KV-PALLADAM-SADAYAPALAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 16:27 | TANTRANSCO | Correct Operation | CAT,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
466 | 230KV-METTUR2-SALEM_TN-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 16:48 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
467 | 230KV-MYVADI-UDUMALPET-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 16:59 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
468 | 230KV-Chekkanurani-NALLAMANAICKENPATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 17:48 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
469 | 230KV-Chekkanurani-SEMBATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 18:40 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
470 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 20:03 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
471 | 230KV-KAYATHAR(TN)-TTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-05-2026 | 01:34 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
472 | 230KV-MAPS-S P KOIL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-05-2026 | 12:00 | NPCIL_MAPS |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
473 | 230KV-KAVANUR-MILAVITTAN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-05-2026 | 15:23 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
474 | 230KV-MYVADI-O.K.MANDAPAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-05-2026 | 05:01 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
475 | 230KV-HOSUR_PG-UDANAPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-05-2026 | 04:20 | PGCIL SR-2 | Correct Operation | AR Successful both ends on Yph-G transient Fault in Line. 2.0 km / 17.25 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | AR Successful both ends on Yph-G transient Fault in Line
476 | 230KV-STCMS-DEVIAKURICHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-05-2026 | 13:24 | TANTRANSCO | Correct Operation | idly charged from Deviakuruchi |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
477 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-05-2026 | 16:04 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
478 | 230KV-MTPS_ST_III-THINGALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-05-2026 | 20:04 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | CAT,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
479 | 230KV-GOBI-ANTHIYUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-05-2026 | 20:36 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
480 | 230KV-KARAIKUDI(TN)-KAVANUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 06-05-2026 | 23:59 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
481 | 230KV-O.K.MANDAPAM-ANAIKADAVU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 05:58 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
482 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 21:32 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
483 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 23:30 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
484 | 230KV-KAVANUR-KAMUDHI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-05-2026 | 05:30 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
485 | 230KV-Chekkanurani-NALLAMANAICKENPATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-05-2026 | 05:34 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
486 | 230KV-O.K.MANDAPAM-ANAIKADAVU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-05-2026 | 06:05 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
487 | 230KV-Chekkanurani-NALLAMANAICKENPATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-05-2026 | 17:57 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
488 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-05-2026 | 20:32 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
489 | 230KV-KARAIKUDI(TN)-KAVANUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-05-2026 | 03:17 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
490 | 230KV-VEERANAM-KODIKURCHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-05-2026 | 02:34 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
491 | 230KV-KAYATHAR(TN)-VEERANAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 10-05-2026 | 20:25 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
492 | 230KV-ARNI-KANCHIPURAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-05-2026 | 10:42 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | Idly charged from Arni |  |  | TRANSIENT FAULT
493 | 230KV-KAVANUR-KAMUDHI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-05-2026 | 22:39 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
494 | 220KV-NAGJHERI-BIDNAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 17-05-2026 | 17:25 | KPCL |  |  |  |  | KPTCL |  | Zone-1, R-phase, Ia=4.065kA, diastnce=30.65km |  |  | Transient fault.. No fault found due to heavy wind & rain.
495 | 230KV-SALEM_TN-SINGIPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 13-05-2026 | 12:39 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | CAT,R,NAR SUCCESSFUL |  |  | TRANSIENT FAULT
496 | 230KV-KAYATHAR-SANGRAPERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-05-2026 | 12:23 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | DT RECEIVED |  |  | TRANSIENT FAULT
497 | 230KV-ARASUR-PUSHEP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 14-05-2026 | 16:50 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNGECL |  |  |  |  | TRANSIENT FAULT
498 | 230KV-VEERAPURAM-CUDDALORE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-05-2026 | 12:26 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | Idly charged from Veerapuram |  |  | TRANSIENT FAULT
499 | 230KV-VEERAPURAM-CUDDALORE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-05-2026 | 12:18 | TANTRANSCO | Correct Operation | Idly charged from cuddalore |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
500 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-05-2026 | 19:24 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
501 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 01-05-2026 | 13:19 | TGGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
502 | 230KV-KARAIKUDI(TN)-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-05-2026 | 05:39 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
503 | 230KV-KAYATHAR(TN)-KINNIMANGLAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-05-2026 | 18:09 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
504 | 220KV-SRISAILAM_RIGHT_BANK-MARKAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 01-05-2026 | 14:28 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
505 | 230KV-Chekkanurani-NALLAMANAICKENPATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-05-2026 | 18:33 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
506 | 400KV-SURYAPET-KV_KOTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | APTRANSCO | 01-05-2026 | 14:53 | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | APTRANSCO | Correct Operation
507 | 230KV-VEERAPURAM-CUDDALORE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 16-05-2026 | 05:55 | TANTRANSCO | Correct Operation | idly charged from Cuddalore |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
508 | 230KV-TTPS-ANUPANKULAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 16-05-2026 | 23:39 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
509 | 230KV-KAYATHAR(TN)-KINNIMANGLAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-05-2026 | 00:55 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
510 | 230KV-KAVANUR-VALATHUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-05-2026 | 02:16 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
511 | 230KV-KARAIKUDI(TN)-KAVANUR-3 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-05-2026 | 02:52 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
512 | 230KV-KAYATHAR(TN)-TTPS-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-05-2026 | 05:43 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
513 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-05-2026 | 21:03 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
514 | 230KV-THIRUVARUR-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-05-2026 | 05:28 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,Y,N_PD operated | AR Close pulse output contact defect in sifang relay. New output card arranged. Line clear awaited | Pending | TRANSIENT FAULT
515 | 230KV-SAMAYAPURAM-TRICHY(TN)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-05-2026 | 05:48 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
516 | 230KV-UDUMALPET-ALIYAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-05-2026 | 12:34 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
517 | 230KV-KARAIKUDI-PUDUKKOTTAI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-05-2026 | 16:35 | PGCIL SR-2 | Correct Operation | AR Successful both ends on Yph-G Fault in Line. 10 km / 9.8 kA |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | AR Successful both ends on Yph-G Fault in Line.
518 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-05-2026 | 21:17 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
519 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-05-2026 | 21:45 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
520 | 230KV-TIRUNELVELI-UDAYATHOOR | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-05-2026 | 12:25 | PGCIL SR-2 | Correct Operation | AR Successful both ends - 19.2 km / 5.01 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | AR Successful both ends Rph-G Fault in Line.
521 | 230KV-MTPS_ST_III-THINGALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-05-2026 | 23:41 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
522 | 220KV-PENDURTHI-UPPER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 01-05-2026 | 11:30 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | C-Phase to earth with AR operated |  |  | C-Phase to earth with AR operated at USPH end
523 | 220KV-VTPS-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 01-05-2026 | 12:49 | APGENCO | Correct Operation | Bph-G fault , Zone-1 distance protection operated. |  |  | APTRANSCO | Correct Operation |  |  |  | distance protection operated
524 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-05-2026 | 02:53 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
525 | 400KV-MARADAM-KALPAKKA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 01-05-2026 | 15:20 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
526 | 220KV-PARAVADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 01-05-2026 | 17:45 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
527 | 230KV-PALAVADI-UDANAPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-05-2026 | 21:34 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,R,N,_AR operated in lockout | AR Closure scheme has to be checked in next LC | Pending | TRANSIENT FAULT
528 | 220KV-PARAVADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 02-05-2026 | 03:29 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
529 | 220KV-GOOTY-SWS-ULTRATECH-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 02-05-2026 | 06:16 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
530 | 220KV-PARAVADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 02-05-2026 | 09:45 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
531 | 220KV-BHIMADOLE-PALLANTLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 02-05-2026 | 10:45 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
532 | 220KV-NELLORE_AP-RACHAGUNNERI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 02-05-2026 | 13:26 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
533 | 220KV-ANANTHAPUR-THIMAPRAM_LI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 02-05-2026 | 14:12 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
534 | 220KV-GARIVIDI-BOBBILI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 02-05-2026 | 16:17 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
535 | 230KV-Chekkanurani-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 25-05-2026 | 03:33 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
536 | 220KV-PALLANTLA-GUDDIGUDEM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 02-05-2026 | 16:43 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
537 | 220KV-PENDURTHI-UPPER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 04:41 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | b-Phase to Earth @Z-1 operated |  |  | b-Phase to Earth @Z-1 operated
538 | 220KV-NIDADAVOLU-PALLANTLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 08:52 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
539 | 400KV-VEMAGIRI_PG-VEMAGIRI_AP-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 09:01 | PGCIL SR-1 | Correct Operation |  |  |  | APTRANSCO | Correct Operation
540 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 10-05-2026 | 03:42 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
541 | 220KV-SULURPET-NELLORE_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 10:15 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
542 | 220KV-KV_KOTA_OLD-NUZVID-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 11:43 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
543 | 220KV-CHITTOOR-KALIKIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 12:00 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
544 | 400KV-SATTENPALLY-PODILI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 03-05-2026 | 13:56 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
545 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 03-05-2026 | 14:04 | TGGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | single phase fault
546 | 220KV-NELLORE_AP-RACHAGUNNERI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 14:09 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
547 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_AP-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 16:20 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
548 | 220KV-ATMAKUR-PODILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 18:04 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
549 | 220KV-ONGOLE-KANDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 20:12 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
550 | 230KV-METTUR2-SALEM_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 26-05-2026 | 20:11 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
551 | 220KV-ONGOLE-PODILI_OLD-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 20:13 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
552 | 230KV-KARAIKUDI(TN)-KAVANUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 26-05-2026 | 23:33 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
553 | 220KV-NELLORE_AP_OLD-ATMAKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 20:21 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
554 | 230KV-Chekkanurani-KAYATHAR(TN)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-05-2026 | 05:54 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
555 | 230KV-KARAIKUDI-SEMBATTI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-05-2026 | 18:16 | PGCIL SR-2 | Correct Operation | AR Successful. 6.6 km/ 12.6 kA |  |  | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | AR Successful both substation Rph-G Fault in Line.
556 | 230KV-KARAIKUDI-SEMBATTI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-05-2026 | 18:37 | PGCIL SR-2 | Correct Operation | AR Successful both ends. 21.7 km /6.2 kA. |  |  | TANTRANSCO | Correct Operation | CAT,R,N,AR SUCCESSFUL |  |  | AR Successful Rph-G Fault in Line.
557 | 230KV-KARIMANAGALAAM-PALAVADI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 28-05-2026 | 22:00 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
558 | 220KV-SULURPET-NELLORE_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 21:39 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
559 | 230KV-PALAVADI-UDANAPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 28-05-2026 | 22:29 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,R,N,AR LOCKOUT | AR SCHEME HAS TO BE CHECKED | Pending | TRANSIENT FAULT
560 | 220KV-SULURPET-NELLORE_AP-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 21:39 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
561 | 220KV-SULURPET-NELLORE_AP-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 21:39 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
562 | 220KV-ANIMALA-CHAKRAYAPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 04-05-2026 | 15:56 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
563 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-05-2026 | 15:15 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
564 | 400KV-MARADAM-KALPAKKA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 04-05-2026 | 18:36 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
565 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 05-05-2026 | 13:25 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
566 | 230KV-THUDIYALUR-KARAMADAI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-05-2026 | 22:25 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
567 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 05-05-2026 | 15:39 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
568 | 400KV-VIJAYAWADA-NELLORE_AP-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 19:19 | PGCIL SR-1 | Correct Operation |  |  |  | APTRANSCO | Correct Operation
569 | 220KV-JAMMALAMADUGU-BETAMCHERLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 06-05-2026 | 19:56 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
570 | 400KV-NELLORE_AP-VTPS_IV-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 06-05-2026 | 21:33 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation |  |  |  | NO TRIPPING
571 | 400KV-CHITTOOR-RACHAGUNNERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 09-05-2026 | 11:56 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
572 | 220KV-CHILLAKALLU-PULICHINTALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 10-05-2026 | 13:42 | APTRANSCO | Correct Operation |  |  |  | TGGENCO | Correct Operation |  |  |  | B-ph trip
573 | 220KV-BOYAREDDYPALLI-TADIPATHRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 10-05-2026 | 18:01 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
574 | 220KV-SRISAILAM_RIGHT_BANK-BILAKALAGUDUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 11-05-2026 | 04:39 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
575 | 230KV-ANUPANKULAM-KAYATHAR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 30-05-2026 | 05:33 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
576 | 220KV-NELLORE_AP_OLD-ATMAKUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 11-05-2026 | 08:10 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
577 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 31-05-2026 | 04:00 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
578 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 31-05-2026 | 13:06 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
579 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 11-05-2026 | 13:46 | APTRANSCO | Correct Operation |  |  |  | TGGENCO | Correct Operation
580 | 220KV-GUDIVADA-AKIVEEDU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 11-05-2026 | 18:29 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
581 | 230KV-Chekkanurani-SAVASPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 31-05-2026 | 17:54 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
582 | 220KV-GUNADALA-VTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 12-05-2026 | 13:10 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | R-Ph-Bph ,Zone-1 operated . |  |  | distance protection operated
583 | 220KV-GUDIVADA-AKIVEEDU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 12-05-2026 | 18:29 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
584 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-05-2026 | 10:43 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | B phase jumper cut attended at loc.14.
585 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-05-2026 | 11:01 | TANTRANSCO | Correct Operation | During the incident, Manali end open condition. CMRL end only charged. |  |  | TANTRANSCO | Correct Operation | DEF TRIP |  |  | B phase jumper cut attended at loc.14.
586 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 13-05-2026 | 04:56 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
587 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 13-05-2026 | 10:22 | APTRANSCO | Correct Operation |  |  |  | TGGENCO | Correct Operation
588 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-05-2026 | 18:49 | TANTRANSCO | Correct Operation | ZONE.1,Y,N_AR OFF_COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N_AR OFF_COMPOSITE FEEDER |  |  | At loc.51,Y ph suspension insulator flashover attended
589 | 220KV-KAKINADA-PARAVADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 13-05-2026 | 10:30 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
590 | 220KV-NANSURALLA-MOLAGAVALI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 13-05-2026 | 11:06 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
591 | 220KV-VIJAYAWADA-BHIMADOLE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 15-05-2026 | 14:00 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
592 | 230KV-KORATTUR-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 05-05-2026 | 15:59 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR OFF_ COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.2,R,N,AR OFF_ COMPOSITE FEEDER_ CARRIER FAIL DUE TO FIBRE CUT |  |  | TRANSIENT FAULT
593 | 220KV-PIDUGURALLA-INAPARAJUPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 15-05-2026 | 17:27 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
594 | 220KV-ANANTHAPUR-THIMAPRAM_LI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 16-05-2026 | 16:59 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
595 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 17-05-2026 | 13:48 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
596 | 220KV-PIDUGURALLA-INAPARAJUPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 18-05-2026 | 05:07 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
597 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 05:16 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR OFF_Composite feeder |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR OFF_Composite feeder |  |  | R phase line cut at location: 56
598 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 19-05-2026 | 05:06 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
599 | 220KV-NELLORE_AP_OLD-ATMAKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-05-2026 | 11:00 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
600 | 220KV-VTPS-NUZVID-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 19-05-2026 | 11:54 | APGENCO | Correct Operation | Bph-G fault , Zone-1 distance protection operated,AR Success. |  |  | APTRANSCO | Correct Operation |  |  |  | distance protection operated
601 | 220KV-BD_PALEM-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 08:05 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
602 | 220KV-DAIRYFARM-SIMHACHALM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 11:33 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
603 | 230KV-NCTPS-TONDIARPET-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-05-2026 | 04:32 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N, AR OFF _FEEDER CONSTRAINTS |  |  | TRANSIENT FAULT
604 | 220KV-NIDADAVOLU-PALLANTLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 12:04 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
605 | 220KV-NIDADAVOLU-BOMMUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 13:23 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
606 | 230KV-NCTPS-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-05-2026 | 04:33 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N, AR OFF _FEEDER CONSTRAINTS |  |  | TRANSIENT FAULT
607 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 11-05-2026 | 22:26 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_ COMPOSITE FEEDER_At manali end take off tower B ph jumper cut & earthed towards Manali end |  |  | TANTRANSCO | Correct Operation | holding |  |  | TRANSIENT FAULT
608 | 220KV-JAMMALAMADUGU-THIRUMALAYAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 17:02 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
609 | 220KV-GOOTY-SWS-ANANTHAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 17:08 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
610 | 220KV-JAMMALAMADUGU-THIRUMALAYAPALLI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 17:42 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
611 | 220KV-JAMMALAMADUGU-BETAMCHERLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 18:07 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
612 | 220KV-JAMMALAMADUGU-PORUMAMILA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 18:07 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
613 | 220KV-GOOTY-SWS-ANANTHAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 20-05-2026 | 18:34 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
614 | 220KV-BOMMUR-LOWER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 00:40 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | Jumper cutted in B-Ph T-Joint of breaker isolator |  |  | Bus bar differential protection operated in B-Ph protection relay
615 | 220KV-VIJAYAWADA-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 13:14 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
616 | 220KV-CHILLAKALLU-PULICHINTALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 21-05-2026 | 13:37 | APTRANSCO | Correct Operation |  |  |  | TGGENCO | Correct Operation |  |  |  | B-ph trip
617 | 220KV-BOBBILI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 13:53 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
618 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 21-05-2026 | 13:58 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
619 | 220KV-PARCHOOR-SATTENPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 18:47 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
620 | 220KV-PARCHOOR-SATTENPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 19:15 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
621 | 220KV-NARNOOR-BRAMHANA_KOTKUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 21:52 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
622 | 220KV-KAKINADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 21:58 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
623 | 220KV-APCARBIDE-NARNOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 22:08 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
624 | 220KV-APCARBIDE-NARNOOR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 21-05-2026 | 22:08 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
625 | 230KV-KORATTUR-CONTROL_DATA_CENTRE_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-05-2026 | 13:35 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_Composite feeder |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_Composite feeder |  |  | TRANSIENT FAULT
626 | 230KV-KORATTUR-MANALI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-05-2026 | 13:50 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR OFF_Composite feeder |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR OFF_Composite feeder |  |  | TRANSIENT FAULT
627 | 220KV-PULIVENDULA-GOLLAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 00:37 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
628 | 220KV-GADDAMVARIPALLI-GODDUMARRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 02:08 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
629 | 220KV-SRISAILAM_RIGHT_BANK-MYDUKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 22-05-2026 | 02:13 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
630 | 220KV-CUDDAPAH-RAYALSEEMA TPP-4 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 02:15 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | ZONE-1, Rph to G, Zone-1 protection optd. |  |  | Transient fault
631 | 220KV-ANANTHAPUR-KALYANDURGA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 02:25 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
632 | 220KV-ANANTHAPUR-KALYANDURGA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 02:32 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
633 | 220KV-GOOTY-SWS-SHAPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 07:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
634 | 220KV-GOOTY-SWS-DHONE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 07:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
635 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-05-2026 | 08:13 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TRANSIENT FAULT
636 | 220KV-GOOTY-SWS-BOYAREDDYPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 07:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
637 | 230KV-MANALI-CMRL_CENTRAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-05-2026 | 12:32 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TOWER COLLAPSED @LOC.NO.36. Line restored on 14-06-2026 at 16:04hrs
638 | 220KV-GOOTY-SWS-GOOTY-RLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 07:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
639 | 220KV-GOOTY-SWS-ULTRATECH-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 07:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
640 | 220KV-VTPS-RENTACHINTHALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 08:05 | APGENCO | Correct Operation | Yph-Bph fault, Z-1 protection operated. |  |  | APTRANSCO | Correct Operation |  |  |  | distance protection operated
641 | 230KV-MYVADI-SEMBATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-05-2026 | 08:10 | TANTRANSCO | Correct Operation | CAT,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | Tree clearance done at location 205-206_ coconut tree fell down due to heavy rain and wind
642 | 220KV-GAZUWAKA_AP-PENDURTHI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 12:20 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
643 | 220KV-CHITTOOR-NAGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 13:01 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
644 | 230KV-Chekkanurani-SAVASPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-05-2026 | 12:52 | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TRANSIENT FAULT
645 | 220KV-RAMPACHODAVARAM-BAVOJIPETA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 14:40 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
646 | 220KV-VIZAG_SWS-PARAVADA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 15:15 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
647 | 220KV-BOBBILI-MARADAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 18:31 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
648 | 230KV-KARAIKUDI-SEMBATTI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-05-2026 | 18:05 | PGCIL SR-2 | Correct Operation | Line tripped on Rph-Yph ( Ph-Ph-G) Fault in line. 147 km / 1.21 kA, 1.41 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | At location no .119 , R - ph jumper cone cut attened
649 | 220KV-GARIVIDI-BOBBILI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 18:32 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
650 | 230KV-MTPS_ST_III-THINGALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-05-2026 | 12:56 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TRANSIENT FAULT
651 | 220KV-GARIVIDI-BOBBILI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 18:32 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
652 | 220KV-BD_PALEM-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 18:46 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
653 | 230KV-KARAMADAI-KARUVALUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 14:58 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | CAT,R,N,TOR |  |  | TRANSIENT FAULT
654 | 220KV-BOBBILI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 18:46 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
655 | 220KV-PENDURTHI-UPPER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 20:20 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | LC issued to PNDT Lines AE for break down maintenance |  |  | tripped on Y Phase - to Earth,z-1,SOTF, and carrier send to PNDT
656 | 230KV-ARASUR_PG-ARASUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 15:25 | PGCIL SR-2 | Correct Operation | Line tripped on B -G fault. AR Attempted and tripped on TOR. 1.436 km / 19.43 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | OPGW cable cut in between location 6 & 7 attended
657 | 220KV-HINDUPUR-GORANTLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 22-05-2026 | 23:08 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
658 | 220KV-KANDUKUR-RACHARLAPADU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 06:19 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
659 | 230KV-ALAMATHY-OPG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-05-2026 | 11:35 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
660 | 220KV-KALPAKKA-SIMHACHALM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 12:52 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
661 | 220KV-PARAVADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 13:08 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
662 | 220KV-BOBBILI-MARADAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 14:23 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
663 | 220KV-NARNOOR-BRAMHANA_KOTKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 18:26 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
664 | 220KV-NANSURALLA-PENDEKOLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 23-05-2026 | 20:10 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
665 | 220KV-VIJAYAWADA-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 10:44 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
666 | 220KV-NIDADAVOLU-PALLANTLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 12:00 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
667 | 220KV-RAMPACHODAVARAM-BAVOJIPETA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 12:04 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
668 | 220KV-NIDADAVOLU-KV_KOTA_OLD-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 13:07 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
669 | 220KV-NIDADAVOLU-PALLANTLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 13:08 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
670 | 220KV-KAKINADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 13:15 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
671 | 220KV-SHAPURNAGAR-RAYADURG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 03-05-2026 | 12:46 | TGTRANSCO | Correct Operation | Correcet operation |  |  | TGTRANSCO | Correct Operation | Breaker problem reported at Rayadurg end and rectified |  |  | TRIPPED ON B-N FAULT
672 | 220KV-BOMMUR-KAKINADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 13:54 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
673 | 220KV-GACHIBOWLI-RAYADURG-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 03-05-2026 | 13:28 | TGTRANSCO | Correct Operation | Composite Line |  |  | TGTRANSCO | Correct Operation | Composite Line |  |  | TRIPPED ON B-N FAULT
674 | 400KV-GAUTAMI-VEMAGIRI_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 24-05-2026 | 14:13 | APGENCO |  |  |  |  | APTRANSCO | Correct Operation
675 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 24-05-2026 | 15:27 | TGGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | single phase fault
676 | 220KV-VIJAYAWADA-TIRUVURU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 18:02 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
677 | 400KV-VIJAYAWADA-NELLORE_AP-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 24-05-2026 | 18:26 | PGCIL SR-1 | Correct Operation |  |  |  | APTRANSCO | Correct Operation
678 | 220KV-GUNADALA-VTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 19:13 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | Y-ph -G fault ,Z-1 protection operated. |  |  | distance protection operated
679 | 220KV-WANAPARTHY-BRAMHANA_KOTKUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 04-05-2026 | 05:25 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | APTRANSCO | Correct Operation |  |  |  | TRIPPED ON B-N FAULT
680 | 220KV-KAKINADA-ANRAK-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 29-05-2026 | 10:37 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
681 | 220KV-CHITTOOR-PALAMANERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 29-05-2026 | 18:46 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
682 | 220KV-NIRMAL-MUPKAL-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 04-05-2026 | 14:01 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON B-N FAULT
683 | 220KV-GOOTY-SWS-ULTRATECH-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-05-2026 | 16:05 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
684 | 400KV-RAYALSEEMA TPP-KALIKIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 30-05-2026 | 16:08 | APGENCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation |  |  |  | SLG fault
685 | 220KV-PENDURTHI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 30-05-2026 | 19:42 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
686 | 220KV-GARIVIDI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 31-05-2026 | 04:40 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
687 | 220KV-VTPS-NUZVID-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 31-05-2026 | 12:44 | APGENCO | Correct Operation | Yph-Bph fault ,Z-1 protection operated. |  |  | APTRANSCO | Correct Operation |  |  |  | distance protection operated
688 | 220KV-KRISHNAGIRI-REGEN-PS_KRISHNAGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 31-05-2026 | 15:20 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
689 | 220KV-CHITTOOR-NAGIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 31-05-2026 | 17:07 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
690 | 220KV-VIJAYAWADA-GUDIVADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 20:29 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
691 | 220KV-VIJAYAWADA-GUDIVADA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 20:29 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
692 | 220KV-PODILI_OLD-MARKAPUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 24-05-2026 | 20:38 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
693 | 230KV-SRIPERUMBADUR_TN-L&T_DATA_CENTRE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-05-2026 | 12:15 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
694 | 230KV-KOYAMBEDU-SRIPERUMBADUR_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-05-2026 | 14:45 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR OFF_COMPOSITE FEEDER |  |  | TRANSIENT FAULT
695 | 230KV-THIRUVARUR-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-05-2026 | 11:45 | TANTRANSCO | Correct Operation | ZONE.1.B,N,TOR |  |  | TANTRANSCO | Failure Operation | ZONE.1.B,N_PD Operated | AR Close pulse output contact defect in sifang relay. New output card arranged. Line clear awaited | Pending | TRANSIENT FAULT
696 | 220KV-MALYALAPALLI-MANDAMARRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 06-05-2026 | 10:05 | TGTRANSCO | Correct Operation | Correct operation |  |  | TGTRANSCO | Correct Operation | Correct operation |  |  | Tripped on Y&B fault
697 | 230KV-KARAIKUDI(TN)-KARAMBAYAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-05-2026 | 12:49 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
698 | 230KV-TIRUPPUR-PALLADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-05-2026 | 16:17 | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | Replacing of Flashed Suspension Insulator at Loc 170
699 | 230KV-KARAIKUDI(TN)-KAVANUR-4 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-05-2026 | 03:27 | TANTRANSCO | Failure Operation | ZONE.1,R,N,PD OPERATED | Breaker mechanism checked on 05/06/2026 | Completed | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR | Breaker mechanism checked on 05/06/2026 |  | TRANSIENT FAULT
700 | 400KV-RAYALSEEMA TPP-KALIKIRI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 25-05-2026 | 04:45 | APGENCO | Correct Operation | Auto Reclosure successful operation |  |  | APTRANSCO | Correct Operation |  |  |  | SLG fault
701 | 230KV-KAVANUR-MILAVITTAN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-05-2026 | 14:14 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | Loc no 186 Y ph Disc replaced
702 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 25-05-2026 | 11:09 | APTRANSCO | Correct Operation |  |  |  | TGGENCO | Correct Operation
703 | 220KV-VIJAYAWADA-GUDIVADA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-05-2026 | 11:10 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
704 | 220KV-VTPS-NUZVID-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-05-2026 | 11:16 | APGENCO | Correct Operation | B-PH, Z-1 ,AR OPERATED AND SUCCESS. |  |  | APTRANSCO | Correct Operation |  |  |  | distance protection operated
705 | 230KV-PARAMATHY-VALAYAPATTY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 07-05-2026 | 22:26 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | At loaction. 306 Y Phase suspention disc decaped and fell on the Tower itself
706 | 220KV-VIJAYAWADA-KOTHAGUDEM_TPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | APTRANSCO | 25-05-2026 | 14:28 | APTRANSCO | Correct Operation |  |  |  | TGGENCO | Correct Operation
707 | 230KV-KARAIKUDI(TN)-KAVANUR-4 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 12-05-2026 | 04:57 | TANTRANSCO | Failure Operation | ZONE.1,R,N_PD Operated | Breaker mechanism checked on 05/06/2026 | Completed | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR | Breaker mechanism checked on 05/06/2026 |  | TRANSIENT FAULT
708 | 220KV-VTPS-RENTACHINTHALA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 25-05-2026 | 16:47 | APGENCO | Correct Operation | Yph-Bph fault ,Z-1 protection operated. |  |  | APTRANSCO | Correct Operation |  |  |  | distance protection operated
709 | 220KV-NELLORE_AP_OLD-NELLORE_AP-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-05-2026 | 10:05 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
710 | 230KV-KAYATHAR(TN)-VEERANAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 15-05-2026 | 21:21 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | at Loc.54 R ph Disc Flahover
711 | 220KV-PENDURTHI-UPPER_SILERU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-05-2026 | 17:01 | APTRANSCO | Correct Operation |  |  |  | APGENCO | Correct Operation | AR operated |  |  | B-Phase to Earth fault operated
712 | 230KV-KARAIKUDI(TN)-KAVANUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 17-05-2026 | 05:49 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
713 | 220KV-PENDURTHI-MARADAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-05-2026 | 17:30 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
714 | 220KV-MARADAM-PYDIBHIMAVARAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-05-2026 | 17:56 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
715 | 230KV-KARAIKUDI(TN)-KAVANUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 18-05-2026 | 11:54 | TANTRANSCO | Correct Operation | holding |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | At Location 96 Y ph jumper cut
716 | 220KV-MARADAM-PYDIBHIMAVARAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-05-2026 | 17:35 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
717 | 220KV-JAMMALAMADUGU-BETAMCHERLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-05-2026 | 20:33 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
718 | 220KV-VTPS-RENTACHINTHALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-05-2026 | 22:33 | APGENCO | Correct Operation | Bph-G fault,Z-2 protection operated. |  |  | APTRANSCO | Correct Operation |  |  |  | distance protection operated.
719 | 220KV-ANANTHAPUR-KALYANDURGA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-05-2026 | 23:50 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
720 | 220KV-DINDI-DOMALAPENTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 11-05-2026 | 16:39 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON B-N FAULT
721 | 230KV-KADALANGUDI-PP_NALUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-05-2026 | 15:25 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | Loc.72 conductor snapped from tension fitting in Y-phase & line decapped
722 | 220KV-KOTHAGUDEM_TPS-MIRYALAGUDA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 12-05-2026 | 01:58 | TGGENCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON R-N FAULT
723 | 220KV-VTPS-CHILLAKALLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 26-05-2026 | 23:53 | APGENCO | Correct Operation | Bph-G fault ,Z-1 protection operated,AR disabled. |  |  | APTRANSCO | Correct Operation |  |  |  | distance protection operated
724 | 220KV-CHILLAKALLU-PULICHINTALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Inter | TGTRANSCO | 26-05-2026 | 23:53 | APTRANSCO | Correct Operation |  |  |  | TGGENCO | Correct Operation |  |  |  | Zone 5 3-phase trip
725 | 220KV-PENDURTHI-MARADAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-05-2026 | 00:25 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
726 | 220KV-CHITTOOR-PALAMANERU-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-05-2026 | 00:51 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
727 | 230KV-TIRUVALAM_TN-KANCHIPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-05-2026 | 21:25 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | Snapping of conductor bet Location no. 116 &117
728 | 220KV-ONGOLE-PODILI_OLD-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-05-2026 | 03:01 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
729 | 400KV-NARNOOR-MAHESHWARAM_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 27-05-2026 | 03:20 | APTRANSCO | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation |  |  |  | A/R successful B-N fault.
730 | 220KV-VIZAG_SWS-PENDURTHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-05-2026 | 04:25 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
731 | 220KV-DICHPALLY_OLD-MEDARAM_TG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 16-05-2026 | 12:28 | TGTRANSCO | Correct Operation | Correct Operation |  |  | TGTRANSCO | Correct Operation | Correct Operation |  |  | Tripped on R&Y fault
732 | 220KV-GAZUWAKA_AP-PENDURTHI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-05-2026 | 04:27 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
733 | 220KV-PENDURTHI-BD_PALEM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 27-05-2026 | 04:27 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
734 | 220KV-JEGURUPADU-NIDADAVOLU-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-05-2026 | 20:05 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
735 | 230KV-Chekkanurani-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-05-2026 | 05:04 | TANTRANSCO | Unwanted Operation | LDP_R PHASE_M2 circuit CT Secondary circuit wire from junction box to relay panel got short circuited, resulting in the operation of differential protection | The same was attended at Checkarunni end | Completed | TANTRANSCO | Correct Operation | LDP_R PHASE |  |  | M2 circuit CT Secondary circuit wire from junction box to relay panel got short circuited, resulting in the operation of differential protection
736 | 220KV-SIRSI-SHARAVATHY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | KPTCL | 12-05-2026 | 19:22 | KPTCL | Correct Operation | Zone-1, B-phase, distance=33.91km,TOR at Shimoga end |  |  | KPCL |  |  |  |  | Transient fault
737 | 230KV-KARAIKUDI-SEMBATTI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 23-05-2026 | 16:55 | PGCIL SR-2 | Correct Operation | AR attempted but Line tripped on Bph- G. |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | Line tripped due to Trip on reclose on Bph-G transient fault in line.
738 | 220KV-RAYALSEEMA TPP-YERRAGUNTLA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-05-2026 | 21:00 | APGENCO | Correct Operation | Y-N FAULT ZONE-1, protection optd. |  |  | APTRANSCO | Correct Operation |  |  |  | Transient fault
739 | 220KV-RAYALSEEMA TPP-YERRAGUNTLA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-05-2026 | 21:00 | APGENCO | Correct Operation | Y-N FAULT ZONE-1, protection operated |  |  | APTRANSCO | Correct Operation |  |  |  | Transient fault
740 | 220KV-JAMMALAMADUGU-ANIMALA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-05-2026 | 21:25 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
741 | 230KV-ARNI-SINGARPET | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-05-2026 | 13:53 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR
742 | 220KV-JAMMALAMADUGU-PORUMAMILA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 28-05-2026 | 21:31 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
743 | 230KV-KAYATHAR(TN)-KINNIMANGLAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-05-2026 | 16:00 | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TRANSIENT FAULT
744 | 230KV-SRIPERUMBADUR_TN-L&T_DATA_CENTRE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 27-05-2026 | 15:19 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
745 | 400KV-THALLAYAPALEM-SATTENPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | APTRANSCO | 28-05-2026 | 22:36 | APTRANSCO | Failure Operation |  |  | Pending | APTRANSCO | Correct Operation
746 | 400KV-NARNOOR-MAHESHWARAM_PG-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Inter | POWERGRID | 29-05-2026 | 04:40 | APTRANSCO | Correct Operation |  |  |  | PGCIL SR-1 | Correct Operation
747 | 230KV-ARNI-SINGARPET | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 28-05-2026 | 20:37 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N,TOR |  |  | TRANSIENT FAULT
748 | 230KV-SRIPERUMBADUR_TN-SURYA_DEV-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-05-2026 | 13:28 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | Idly charged from Sriperumpudhur |  |  | TRANSIENT FAULT
749 | 400KV-VIJAYAWADA-NELLORE_AP-3 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | POWERGRID | 03-05-2026 | 19:51 | PGCIL SR-1 | Correct Operation |  |  |  | APTRANSCO | Correct Operation
750 | 220KV-KOTHAGUDEM_TPS-MIRYALAGUDA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 18-05-2026 | 01:48 | TGGENCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON B-N FAULT
751 | 220KV-MALYALAPALLI-DURSHED-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 21-05-2026 | 13:02 | TGTRANSCO | Correct Operation | Correct operation |  |  | TGTRANSCO | Correct Operation | Correct operation |  |  | Tripped on Y&B fault
752 | 220KV-KHAMMAM_TS-WADDEKOTHAPALLE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 21-05-2026 | 14:17 | TGTRANSCO | Correct Operation | Correct Operation |  |  | TGTRANSCO | Correct Operation | Correct Operation |  |  | Tripped on R&Y fault
753 | 220KV-KHAMMAM_TS-WADDEKOTHAPALLE-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 21-05-2026 | 14:21 | TGTRANSCO | Correct Operation | Correct Operation |  |  | TGTRANSCO | Correct Operation | Correct Operation |  |  | Tripped on R&Y fault
754 | 220KV-NIRMAL_OLD-JAGITIYAL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 22-05-2026 | 10:20 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON B-N FAULT
755 | 220KV-JAGITIYAL-VEMNOOR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 22-05-2026 | 11:38 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON Y-N FAULT
756 | 220KV-BHIMGANAPUR-GANGARAM-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 22-05-2026 | 12:45 | TGTRANSCO | Correct Operation | Correct Operation |  |  | TGTRANSCO | Correct Operation | Correct Operation |  |  | Tripped on Y-B fault
757 | 220KV-NIRMAL_OLD-JAGITIYAL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 22-05-2026 | 15:17 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON B-N FAULT
758 | 220KV-KHAMMAM_TS-WADDEKOTHAPALLE-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 23-05-2026 | 13:57 | TGTRANSCO | Correct Operation | Correct Operation |  |  | TGTRANSCO | Correct Operation | Correct Operation |  |  | Tripped on R&Y fault
759 | 220KV-DINDI-KONDAMALLEPALLY-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 23-05-2026 | 16:29 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON R-N FAULT
760 | 400KV-MALKARAM-SURYAPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 01-05-2026 | 22:17 | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | TGTRANSCO | Correct Operation | AR operated Successfully |  |  | R PHASE FAULT
761 | 400KV-SURYAPET-KETHIREDDYPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 03-05-2026 | 16:10 | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | TGTRANSCO | Correct Operation | AR operated successfully |  |  | B-PH FAULT
762 | 400KV-SURYAPET-KETHIREDDYPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 03-05-2026 | 16:12 | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | B-PH FAULT
763 | 400KV-KETHIREDDYPALLY-SHANKARAPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 11-05-2026 | 14:58 | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | B-PH FAULT
764 | 400KV-MAHESHWARAM_TG-DINDI-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 21-05-2026 | 17:56 | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | TGTRANSCO | Correct Operation | AR operated successfully |  |  | R PHASE FAULT
765 | 400KV-GAJWEL-CHANDALAPUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 400 | Intra | TGTRANSCO | 21-05-2026 | 21:22 | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | TGTRANSCO | Correct Operation | AR OPERATED SUCESSFULLY |  |  | R PHASE FAULT
766 | 220KV-JANAGAON-DEVANNAPET-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 25-05-2026 | 16:38 | TGTRANSCO | Correct Operation | Replaced the Broken Hanger rod at Loc No 54 and Flash overed discs at Loc.Nos. 56,57&58 |  |  | TGTRANSCO | Correct Operation | Replaced the Broken Hanger rod at Loc No 54 and Flash overed discs at Loc.Nos. 56,57&58 |  |  | Tripped R&Y fault
767 | 220KV-SHADNAGAR-KETHIREDDYPALLY-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 27-05-2026 | 00:00 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON R-N FAULT
768 | 220KV-BONGULUR-MAHESHWARAM_TG-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 27-05-2026 | 00:50 | TGTRANSCO | Correct Operation | Correct Operation |  |  | TGTRANSCO | Correct Operation | correct operation |  |  | Tripped on R&Y fault
769 | 220KV-DINDI-MADGULA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 27-05-2026 | 01:54 | TGTRANSCO | Correct Operation | Correct Operation |  |  | TGTRANSCO | Correct Operation | correct operation |  |  | Tripped on Y&B fault
770 | 220KV-DINDI-MADGULA-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 27-05-2026 | 01:54 | TGTRANSCO | Correct Operation | Correct Operation |  |  | TGTRANSCO | Correct Operation | correct operation |  |  | Tripped on Y&B fault
771 | 220KV-DINDI-DOMALAPENTA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 27-05-2026 | 02:21 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON R-N FAULT
772 | 220KV-DINDI-NAGARKURNOOL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 27-05-2026 | 02:29 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON R-N FAULT
773 | 220KV-KOTHAGUDEM_TPS-MIRYALAGUDA-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 28-05-2026 | 02:09 | TGGENCO | Correct Operation |  |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON B-N FAULT
774 | 220KV-SIDDIPET-DURSHED-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 28-05-2026 | 21:00 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON R-N FAULT
775 | 220KV-MALYALAPALLI-JAGITIYAL-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | TGTRANSCO | 28-05-2026 | 18:41 | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TGTRANSCO | Correct Operation | A/R operated and successful |  |  | TRIPPED ON R-N FAULT
776 | 230KV-TIRUVALAM_TN-MOSUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-05-2026 | 17:21 | TANTRANSCO | Correct Operation | ZONE.1,R,Y,N |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,Y,N |  |  | TRANSIENT FAULT
777 | 220KV-NELLORE_AP_OLD-NELLORE_AP-2 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 20:20 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
778 | 220KV-NELLORE_AP_OLD-NELLORE_AP-1 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 21:33 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
779 | 220KV-NELLORE_AP_OLD-NELLORE_AP-3 | AC_TRANSMISSION_LINE_CIRCUIT | 220 | Intra | APTRANSCO | 03-05-2026 | 21:49 | APTRANSCO | Correct Operation |  |  |  | APTRANSCO | Correct Operation
780 | 230KV-KAVANUR-MILAVITTAN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 14-05-2026 | 05:39 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
781 | 230KV-Chekkanurani-KAYATHAR(TN)-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 14-05-2026 | 17:22 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
782 | 230KV-SALEM_230-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 21-05-2026 | 11:59 | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,AR SUCCESSFUL |  |  | TRANSIENT FAULT
783 | 230KV-STCMS-PERAMBALUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 15:05 | TANTRANSCO | Correct Operation | Idly charged from Perambalur |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR LOCKOUT_AR Lockout due to subsequent fault within reclaim time
784 | 230KV-MANDIPATTI-VELLALAVIDUTHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 17:47 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR Lockout due to subsequent fault within reclaim time |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR Lockout due to subsequent fault within reclaim time |  |  | TRANSIENT FAULT
785 | 230KV-ALAGAR_KOVIL-MANDIPATTI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 17:57 | TANTRANSCO | Failure Operation | ZONE.1,Y,N,AR LOCKOUT due to carrier fail | FOTE defect at Alagarkoil end | Pending | TANTRANSCO | Failure Operation | ZONE.1,Y,N,AR LOCKOUT due to carrier fail | FOTE defect at Alagarkoil end | Pending | TRANSIENT FAULT
786 | 230KV-ALAMATHY-MOSUR-2 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 03-05-2026 | 13:55 | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TRANSIENT FAULT
787 | 230KV-KARAIKUDI-SEMBATTI | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 04-05-2026 | 19:14 | PGCIL SR-2 | Correct Operation | AR attempted tripped on TOR due to Line fault persisting. 64.8 km / 2.5 kA. |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N_AR Lockout due to subsequent fault within reclaim time |  |  | Line tripped on Bph-G Fault in Line. AR attempted tripped on TOR due to Line fault persisting.
788 | 230KV-BASIN_BRIDGE-TONDIARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 03:29 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N_AR OFF_ FIELD CONSTRAINTS |  |  | TRANSIENT FAULT
789 | 230KV-TP SOLAR-SANGANERI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 08-05-2026 | 19:39 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | R phase insulator flashover at location no.304 attended
790 | 230KV-METTURAUTO-PALAVADI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-05-2026 | 13:33 | TANTRANSCO | Correct Operation | ZONE.1,R,N_AR Lockout due to subsequent fault within reclaim time |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N_AR Lockout due to subsequent fault within reclaim time |  |  | TRANSIENT FAULT
791 | 230KV-TTPS-AUTO-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-05-2026 | 18:33 | TANTRANSCO | Unwanted Operation | SOTF Operated for the line fault in 230kV Kinnimangalam_TTPS line | TNC switch defect. Programmed to replace during next line clear | Pending | TNPGCL |  |  |  |  | TRANSIENT FAULT
792 | 230KV-ARNI-SINGARPET | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 22-05-2026 | 18:32 | TANTRANSCO | Correct Operation | ZONE.1,B,N_AR Lockout due to subsequent fault within reclaim time |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N_AR Lockout due to subsequent fault within reclaim time |  |  | TRANSIENT FAULT
793 | 230KV-KAVANUR-KAMUDHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 24-05-2026 | 01:08 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N_AR Lockout due to subsequent fault within reclaim time |  |  | TRANSIENT FAULT
794 | 230KV-SALEM_230-SINGARPET-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 25-05-2026 | 15:15 | TANTRANSCO | Correct Operation | ZONE.1,B,N_AR Lockout due to subsequent fault within reclaim time |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N_AR Lockout due to subsequent fault within reclaim time |  |  | TRANSIENT FAULT
795 | 230KV-SINGARPET-GURUBARAPALLI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 25-05-2026 | 18:52 | TANTRANSCO | Correct Operation | ZONE.1,B,N_AR Lockout due to subsequent fault within reclaim time |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N_AR Lockout due to subsequent fault within reclaim time |  |  | TRANSIENT FAULT
796 | 230KV-MILAVITTAN-OTTAPIDARAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 28-05-2026 | 15:40 | TANTRANSCO | Correct Operation | DEF TRIP_Due to non clearence of fault in 400kV Ottapidaram_Thennampaaty line fault at Thennampatty end, Kanarpatty end clear the fault in Zone.3 |  |  | TANTRANSCO | Correct Operation | holding |  |  | The feeder tripped on DEF for the delayed clearance of fault in 400kV Ottapidaram Thennampatti 2
797 | 230KV-TIRUVALAM_TN-MOSUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-05-2026 | 14:20 | TANTRANSCO | Correct Operation | ZONE.2,R,N_ Carrier found healthy but intermittently failed during tripping. Hence Zone.2 operated | Non Operation of CAT has to be checked |  | TANTRANSCO | Correct Operation | ZONE.1,R,N_ AR lockout due to subsequent fault within reclaim time. |  |  | Jumper cut in R-ph at Location no.4
798 | 230KV-ARNI-SINGARPET | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-05-2026 | 16:42 | TANTRANSCO | Correct Operation | ZONE.3,R,N |  |  | TANTRANSCO | Correct Operation | Zone.3,R,N |  |  | TRANSIENT FAULT
799 | 230KV-MANDIPATTI-VELLALAVIDUTHI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 31-05-2026 | 16:26 | TANTRANSCO | Correct Operation | ZONE.1,Y,N_AR Lockout due to subsequent fault within reclaim time |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,N_AR Lockout due to subsequent fault within reclaim time |  |  | TRANSIENT FAULT
800 | 230KV-TRICHY-THANJAVUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 31-05-2026 | 17:08 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
801 | 230KV-TRICHY-THUVAKUDI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 31-05-2026 | 17:12 | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TANTRANSCO | Correct Operation | ZONE.1,B,N,TOR |  |  | TRANSIENT FAULT
802 | 230KV-Chekkanurani-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 21:03 | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
803 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 21:03 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
804 | 230KV-TTPS-KINNIMANGLAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 20-05-2026 | 18:32 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,R,N,TOR |  |  | TRANSIENT FAULT
805 | 230KV-PASUMALAI-TTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 29-05-2026 | 14:21 | TANTRANSCO | Correct Operation | ZONE.1,R,Y |  |  | TNPGCL |  |  |  |  | TRANSIENT FAULT
806 | 230KV-GUMMIDIPOONDI-NCTPS-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 09-05-2026 | 04:49 | TANTRANSCO | Failure Operation | ZONE.1,R,N_PD OPERATED | Non Operation of AR has to be checked | Pending | TNPGCL
807 | 230KV-Chekkanurani-THENI-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 31-05-2026 | 11:41 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,Y,N_AR LOCKOUT BREAKER ISSUE | A/C SUPPLY FAILURE IN SPRING CHARGE MOTOR CIRCUIT AT THENI SS | Completed | TRANSIENT FAULT
808 | 230KV-NCTPS-SRIPERUMBADUR_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-05-2026 | 13:55 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TRANSIENT FAULT
809 | 230KV-NCTPS-SRIPERUMBADUR_TN-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-05-2026 | 14:35 | TNPGCL |  |  |  |  | TANTRANSCO | Correct Operation | ZONE.1,Y,B |  |  | TRANSIENT FAULT
810 | 230KV-ACHARAPAKAM-VILLUPURAM-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 01-05-2026 | 14:54 | TANTRANSCO | Correct Operation | ZONE.1,Y,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,Y,N,LOCKOUT_due to carrier fail | carrier signal at Villupuram end has to be checked | Pending | TRANSIENT FAULT
811 | 230KV-ALAGAR_KOVIL-SAMAYANALLUR-1 | AC_TRANSMISSION_LINE_CIRCUIT | 230 | Intra | TANTRANSCO | 02-05-2026 | 19:14 | TANTRANSCO | Correct Operation | ZONE.1,R,N,AR SUCCESSFUL |  |  | TANTRANSCO | Failure Operation | ZONE.1,R,N,Lockout due to OLTE issue at Alagarkoil end | OLTE defect at Alagarkoil end has to be attended | Pending | TRANSIENT FAULT