# Draft Report on grid event Tripping of 220kV Bus-2 of 20kV Lower Sileru PH of APGENCO in Southern Region

(To be submitted by RLDC/NLDC during Grid Disturbances/Grid Incidents/Near Miss Event as per IEGC section 37.2 (f))

(आई ई जी सी 37.2 (एफ) के अनुपालन में)

Date (दिनांक): 08-06-2026 19:00

# Event Summary (घटना का सारांश):

As per the reports submitted, while hand tripping the bus coupler at 220kV Lower Sileru PH, 220kV Lower Sileru chintur Line-1, 220kV Asupaka Lower Sileru Line-1 and Lower Sileru Unit-1 which are connected to 220kV Bus-2 of Lower Sileru PH tripped on Directional earth fault protection. Tripping of all these elements led to loss of power supply to 220kV Bus-2 of 20kV Lower Sileru PH

- Time and Date of the Event (घटना का समय और दिनांक:  26-05-2026 00:12

- Event Category (ग्रिड घटना का प्रकार):  GI-1

- Location/Control Area (स्थान/नियंत्रण क्षेत्र): TELANGANA , ANDHRA PRADESH

- Antecedent Conditions (पूर्ववर्ती स्थिति):

| Condition | Pre-Event (घटना पूर्व) | Post Event (घटना के बाद) |
| --- | --- | --- |
| Andhra Pradesh State Demand (MW) | 12018 | 11944 |
| Andhra Pradesh State Generation (MW) | 9518 | 9401 |
| Telangana State Demand (MW) | 9621 | 9591 |
| Telangana State Generation (MW) | 5591 | 5591 |
| Grid Frequency (Hz) | 49.88 | 49.89 |
| SR Demand (MW) | 54164 | 54045 |
| SR Generation (MW) | 55830 | 55670 |

*Pre and post data of 1 minute before and after the event

| Elements under outage |  |
| --- | --- |
| Weather Condition (मौसम स्थिति) | Normal |

At Lower Sileru SS:

- Load and Generation loss (लोड और जेनरेशन हानि):

| Generation Loss (MW) | Load Loss (MW) |
| --- | --- |
| 100.0 MW | 0.0 MW |

- Duration of interruption (रुकावट की अवधि):  0 hours, 35 minutes

# Details of Equipment Failure (if any during the event) (उपकरण विफलता का विवरण):  NA

# List of Elements got tripped during event (प्रमुख ट्रिपिंग)

      - 220KV-ASUPAKA-LOWER_SILERU-1

      - 220KV-LOWER_SILERU-Chintur-1

- Event Analysis (Based on PMU, SCADA & DR) (घटना का विश्लेषण):

As per the reports submitted, at 21:39 hrs Unit-1 was synchronized to the grid on Bus-1, followed by synchronization of Unit-2 at 21:59 hrs on Bus-2, with the Bus Coupler breaker maintained in the open position. At 23:22 hrs, Unit-2 was de-synchronized from the grid on Bus-2, and subsequently at 23:37 hrs, the Bus Coupler breaker was closed as per APLDC instructions. At 00:11 hrs, the 220 kV Bus Coupler breaker opened, and the operator physically verified that all three phases were in the open condition. During this period, BRC and VT fuse failure annunciations were observed on both the Asupaka and Chinthuru feeders, and simultaneously both feeders tripped at the remote end on Directional earth fault protection , with Unit-1 also tripping on earth fault. After receiving the closing code, the 220 kV Chinthuru feeder was hand-tripped and the Asupaka feeder was charged; however, the BRC annunciation did not reset. Thereafter, upon receiving the opening code, the Asupaka feeder was opened at both ends and the Chinthuru feeder was charged, yet the BRC annunciation remained unreset, and a current of 185 A was observed flowing in the R-phase only. Based on these observations, it was concluded that the R-phase limb of the Bus Coupler breaker had not fully opened internally. Tripping of both 220kV Bus-2 connected lines led to loss of power supply to 220kV Lower Sileru Bus-2.

- DR Analysis:

220KV-ASUPAKA-LOWER_SILERU-1

|  | ASUPAKA - 220KV | LOWER_SILERU - 220KV |
| --- | --- | --- |
| Time Sync Issue | No | No |
| DR Analysis | DR Trigger Time:26-05-2026 00:13:15.480 NEUTRAL TOC2 OP TRIPBUS 2 OP, MCB 86A/B TR On 86A OPTD On SRC1 VT FF OP, CB Y PH OPEN On, CB B PH OPEN On CB R PH OPEN On PHASE SELECT MULTI-P, PHASE SELECT CA PHASE SELECT AG Ir (max): 0.24 kA Iy (max): 0.05 kA Ib (max): 0.05 kA Vr (max): 133.01 kV Vy (max): 150.96 kV Vb (max): 148.76 kV DR Trigger Time:26-05-2026 00:13:15.501 86B TRIP OPTD Ir (max): 0.24 kA Iy (max): 0.05 kA Ib (max): 0.05 kA Vr (max): 133.29 kV Vy (max): 149.78 kV Vb (max): 147.54 kV | DR Trigger Time:26-05-2026 00:12:04.600 Brok.Cond. Alarm, R13 M-1 BRC ANN Ir (max): 0.16 kA Iy (max): 0.02 kA Ib (max): 0.02 kA Vr (max): 131.80 kV Vy (max): 140.68 kV Vb (max): 132.46 kV |

LOWER_SILERU - 220KV

|  | LOWER_SILERU - 220KV |
| --- | --- |
| Time Sync Issue | No |
| DR Analysis | DR Trigger Time:26-05-2026 00:12:04.600 Brok.Cond. Alarm, R13 M-1 BRC ANN Ir (max): 0.16 kA Iy (max): 0.02 kA Ib (max): 0.02 kA Vr (max): 131.80 kV Vy (max): 140.68 kV Vb (max): 132.46 kV |

- A) PMU Analysis:

From PMU, no fault is observed during the event.

B) SCADA Analysis:

From SCADA plot, tripping of 220kV Lower Sileru Bus-2 is observed during the event.

- Protection/Operational issues observed (सुरक्षा/परिचालन संबंधी समस्या):

| Constituent | Points for review |
| --- | --- |
| APGENCO | Non opening bus coupler R-pole limb at Lower Sileru. |

- Action Taken/Remedial Measures (सुधारात्मक उपाय):

| Constituent | Remedial Actions |
| --- | --- |
| APGENCO | Opened Bus Coupler braeker both Bus-1 and Bus-2 isolators and charged 220KV Chinthuru feeder at 2.19 Hrs and stood ok. After getting closing code, the 220KV Asupaka feeder charged at 2.34 hrs., and stood ok. |

- RLDC Analysis/Observations (Based on Simulation Studies):

NA

- Restoration Details:

At 02:09 Hrs, the Bus-Coupler Breaker both Bus-1 and Bus-2 isolators opened and the 220KV Lower Sileru-Chinthuru feeder charged on Bus-2 at 02:19 Hrs and the 220KV Lower Sileru-Asupaka feeder charged on Bus-2 at 02:37 Hrs.

# Non-compliance observed (विनियमन का गैर-अनुपालन):

| Sl.No | Issues | Regulation Non-Compliance | Utilities |
| --- | --- | --- | --- |
| 1 | Flash Report not received within 8 Hours | IEGC section 37.2 (b) | APGENCO |
| 2 | DR/EL not provided within 24 hours | 1. IEGC section 37.2 (c) 2. CEA grid Standard 15.3 |  |
| 3 | Detailed Report not received within 7 days | IEGC section 37.2 (e) |  |
| 4 | Any other non-compliance | IEGC section 17.3 |  |

- Key Lessons Learnt (प्रमुख अधिगम बिंदु):

NA

Annexure 1

Sequence of Events as per SCADA

Annexure 2

SLD of the affected Sub-station/Connectivity Diagram: