## P-Rec (Pending)
Status of Pending Implementation of PCSC Recommendations
Meeting Index | Details of Event | Date & Time | Reason | PCSC Recommendations | Utility Responsible for Implementation | Consolidated Status of Implementation | Individual Compliance Status | Consolidated Compliance Status
MULTI-UTILITIES
141/I/1 | Complete outage of 230kV SR Pudur SS of TANTRANSCO SS. | 22-02-2026 04:15 | As per the reports submitted, 230kV SR Pudur SS is operating with single bus configuration. At 4:15hrs Y-G fault was observed in 230kv SR Pudur Sanganeri line and the line tripped. At 4:57hrs, R-G fault was observed in 230kV Kudankulam SR Pudur line and the line tripped. After tripping of both 230kV ines, 230kV SR Pudur bus was charged through 110kV lines from Udayathur and Sanganeri SS. Eventually, 110kV lines tripped on over loading at remote ends and this led to complete outage of 230kV SR Pudur SS. | 1.TANTRANSCO to revise A/r dead time of all feeders at 230kV Sanganeri SS to 1 Sec. 2.TANTRANSCO to ensure Double bus operation of all 220kV & Substations. 3.TANTRANSCO to rectify the DR time sychronization issue at SR Pudur 4.TANTRANSCO to furnish DR at Sangareni end during the incident | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:45:23: 1.dead time revised to 1 sec 2. Action is being taken to implement the double bus operation wherever feasible 3.GPS is available & IEDs sync with GPS 4. since old relay 3sec DR could not be assign . It is proposed to replace old relay with spare one . Awaiting LIne clear cepc:TANTRANSCO: 05/06/2026 13:43:06: 1. Complied 2. Action is being taken 3.complied 4.Relay replacement will be complied on or before 30.06.2026 | Pending | Pending
141/I/1 | Complete outage of 230kV SR Pudur SS of TANTRANSCO SS. | 22-02-2026 04:15 | As per the reports submitted, 230kV SR Pudur SS is operating with single bus configuration. At 4:15hrs Y-G fault was observed in 230kv SR Pudur Sanganeri line and the line tripped. At 4:57hrs, R-G fault was observed in 230kV Kudankulam SR Pudur line and the line tripped. After tripping of both 230kV ines, 230kV SR Pudur bus was charged through 110kV lines from Udayathur and Sanganeri SS. Eventually, 110kV lines tripped on over loading at remote ends and this led to complete outage of 230kV SR Pudur SS. | NPCIL KKNPP to furnish DR at KKNPP end during the incident | NPCIL KKNPP |  | Pending | Pending
141/II/1 | Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 | 12-02-2026 07:26 | As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operated and all the elements connected to the bus tripped | KPTCL to rectify the DR time sync issue at Neelamanga SS and Yelahanka SS. | KPTCL |  | Pending | Pending
141/II/1 | Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 | 12-02-2026 07:26 | As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operated and all the elements connected to the bus tripped | PGCIL SR-II to report Equipment failure to CEA. | PGCIL SR-II |  | Pending | Pending
141/II/1 | Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 | 12-02-2026 07:26 | As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operated and all the elements connected to the bus tripped | SRLDC to furnsih the reasons for Inphase currents observed during the event and necessary remedial actions to be taken to the forum. | SRLDC | SRLDC_Protection1:SRLDC: 04/05/2026 09:06:34: As deliberated during the meeting, the reason for the in phase currents is due to the zero sequence contribution during fault feeding by radial source. This is a special case where in since the network was radial at LV side and no interconnection such zero sequence currents would be observed and hence any modification in the settings may lead to non operation in genuine cases and would be problematic and the same was deliberated during the meeting. Further remedial actions may be taken after deliberations during the meeting with all entities opinion. | Pending | Pending
141/II/4 | Tripping of 400kV Bus-1 and 2 at Simhadri TPS of NTPC | 25-02-2026 16:03 | The triggering incident is the R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-4 main bay leading to BBP operation and tripping of all the main breakers connected to Bus-2 and 400KV-SIMHADRI-KALPAKKA-4. Subsequently, after around 5s, Bus-1 BBP operated due to R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-3 main bay leading to tripping of all elements connected to 400kV Bus-1 and 2 at Simhadri TPS of NTPC. This led to the tripping of Unit-2 and generation loss of around 420MW. During the event, 400kV Bus-3 and 4 were in service at Simhadri TPS | 1.NTPC Simhadri to expecite the process of replacing porcelien insulator with Polymer insulator. 2.NTPCSimhadri to verify the AR logic at their end and ensure single pole AR operation. | NTPC-Simhadri |  | Pending | Pending
141/II/4 | Tripping of 400kV Bus-1 and 2 at Simhadri TPS of NTPC | 25-02-2026 16:03 | The triggering incident is the R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-4 main bay leading to BBP operation and tripping of all the main breakers connected to Bus-2 and 400KV-SIMHADRI-KALPAKKA-4. Subsequently, after around 5s, Bus-1 BBP operated due to R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-3 main bay leading to tripping of all elements connected to 400kV Bus-1 and 2 at Simhadri TPS of NTPC. This led to the tripping of Unit-2 and generation loss of around 420MW. During the event, 400kV Bus-3 and 4 were in service at Simhadri TPS | APTRANSCO to expedite the OPGW replacement works on Simhadri Kalpakka Line. | APTRANSCO | eesp:APTRANSCO: 01/05/2026 17:17:59: OPGW replacement works on Simhadri-Kalapaka line will be expedited. | Pending | Pending
141/IV/2 | 400KV-KAIGA-GUTTUR-2 | 24-02-2026 15:45 | As per the reports submitted, the triggering incident is the B-G fault in the line. At both ends the fault was sensed in Z1 and at both ends AR did not operate and 3ph tripped. | KPTCL to review the non-operation of Auto reclosure at Guttur end of 400KV-KAIGA-GUTTUR-line 2. | KPTCL |  | Pending | Pending
141/IV/2 | 400KV-KAIGA-GUTTUR-2 | 24-02-2026 15:45 | As per the reports submitted, the triggering incident is the B-G fault in the line. At both ends the fault was sensed in Z1 and at both ends AR did not operate and 3ph tripped. | NPCIL Kaiga to review the non-operation of Auto reclosure at Kaiga end of 400KV-KAIGA-GUTTUR- line 2. | NPCIL Kaiga |  | Pending | Pending
142/I/4 | Complete Outage 220kV Renew_Surya_Koppal of RENEW | 18-03-2026 22:28 | 220kV Renew_Surya_Koppal is connected radially to KOPPAL through 220 kV-KOPPAL-Renew_Surya_Koppal-1. The triggering incident is the R-G fault in the 220 kV-KOPPAL-Renew_Surya_Koppal-1 line and tripping of the only line connected to 220kV Renew_Surya_Koppal led to the Complete Outage 220 kV Renew_Surya_Koppal of RENEW | M/s Indigrid to submit detailed report for the event. M/s Indigrid to submit DR, EL, FIR to SRLDC & SRPC for the event. | M/s Indigrid |  | Pending | Pending
142/I/4 | Complete Outage 220kV Renew_Surya_Koppal of RENEW | 18-03-2026 22:28 | 220kV Renew_Surya_Koppal is connected radially to KOPPAL through 220 kV-KOPPAL-Renew_Surya_Koppal-1. The triggering incident is the R-G fault in the 220 kV-KOPPAL-Renew_Surya_Koppal-1 line and tripping of the only line connected to 220kV Renew_Surya_Koppal led to the Complete Outage 220 kV Renew_Surya_Koppal of RENEW | M/s Renew to enable the Auto reclosure at their end. | M/s Renew |  | Pending | Pending
143/I/1 | Complete Outage of 220kV Lower Sileru of APGENCO | 21-04-2026 22:08 | The triggering incident was a flashover between the contacts of the R-phase breaker in the bus coupler at the 220 kV Lower Sileru Powerhouse during the opening of the bus coupler. Due to this, the LBB protection operated and a DT signal was sent to the remote ends, tripping the lines connected to Bus 1 and Bus 2 of the Lower Sileru Powerhouse at remote ends. This incident led to a complete outage of the Lower Sileru Powerhouse. | APGENCO to disable Direct Transfer Trip (DTT) for manual open commands. TGTRANSCO and APGENCO to do end to end testing for carrier signals for Lower sileru ASUPAKA lines. APGENCO may apprise on status of new breakers at Lower Sileru. | APGENCO |  | Pending | Pending
143/I/1 | Complete Outage of 220kV Lower Sileru of APGENCO | 21-04-2026 22:08 | The triggering incident was a flashover between the contacts of the R-phase breaker in the bus coupler at the 220 kV Lower Sileru Powerhouse during the opening of the bus coupler. Due to this, the LBB protection operated and a DT signal was sent to the remote ends, tripping the lines connected to Bus 1 and Bus 2 of the Lower Sileru Powerhouse at remote ends. This incident led to a complete outage of the Lower Sileru Powerhouse. | TGTRANSCO and APGENCO to do end to end testing for carrier signals for Lower sileru ASUPAKA lines. | TGTRANSCO |  | Pending | Pending
143/I/4 | Complete outage of 400kV UDANGUDI of TNPGCL | 29-04-2026 12:57 | 400kV UDANGUDI SS is radially connected to 400kV OTTAPIDARAM through 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines. Both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines are in the same dia at 400kV Udangudi SS The triggering incident is the B-G fault in 400kV-OTTAPIDARAM-UDANGUDI-1, where in B pole opened. However, due to logic issue implemented in the Tie Breaker led to Tie LBB operation and tripped the other main and led to the tripping of 400kV-OTTAPIDARAM-UDANGUDI-2 and DT was sent to remote. With the tripping of both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 led to the Complete outage of 400kV UDANGUDI of TNPGCL. | TNPGCL to submit detailed report for the event. | TNPGCL |  | Pending | Pending
143/I/4 | Complete outage of 400kV UDANGUDI of TNPGCL | 29-04-2026 12:57 | 400kV UDANGUDI SS is radially connected to 400kV OTTAPIDARAM through 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines. Both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines are in the same dia at 400kV Udangudi SS The triggering incident is the B-G fault in 400kV-OTTAPIDARAM-UDANGUDI-1, where in B pole opened. However, due to logic issue implemented in the Tie Breaker led to Tie LBB operation and tripped the other main and led to the tripping of 400kV-OTTAPIDARAM-UDANGUDI-2 and DT was sent to remote. With the tripping of both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 led to the Complete outage of 400kV UDANGUDI of TNPGCL. | TNSLDC/TANTRANSCO to take up with TNPGCL/TNGEPl for participation. | TNSLDC/TANTRANSCO |  | Pending | Pending
143/I/5 | Complete outage of 400kV UDANGUDI of TNPGCL | 30-04-2026 14:24 | 400kV UDANGUDI is radially connected to 400kV OTTAPIDARAM through 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines. Both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines are in the same dia at 400kV OTTAPIDARAM. The triggering incident is the B-G fault in 400kV-OTTAPIDARAM-UDANGUDI-1, where in B pole opened. However, due to logic issue implemented in the Tie Breaker led to Tie LBB operation and tripped the other main and led to the tripping of 400kV-OTTAPIDARAM-UDANGUDI-2 and DT was sent to remote. With the tripping of both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 led to the Complete outage of 400kV UDANGUDI of TNPGCL during which led to the tripping of unit of Unit-1 UDANGUDI and led to a generation loss of 156MW. | TNPGCL to submit detailed report for the event. | TNPGCL |  | Pending | Pending
143/I/5 | Complete outage of 400kV UDANGUDI of TNPGCL | 30-04-2026 14:24 | 400kV UDANGUDI is radially connected to 400kV OTTAPIDARAM through 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines. Both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 lines are in the same dia at 400kV OTTAPIDARAM. The triggering incident is the B-G fault in 400kV-OTTAPIDARAM-UDANGUDI-1, where in B pole opened. However, due to logic issue implemented in the Tie Breaker led to Tie LBB operation and tripped the other main and led to the tripping of 400kV-OTTAPIDARAM-UDANGUDI-2 and DT was sent to remote. With the tripping of both the 400kV-OTTAPIDARAM-UDANGUDI-1&2 led to the Complete outage of 400kV UDANGUDI of TNPGCL during which led to the tripping of unit of Unit-1 UDANGUDI and led to a generation loss of 156MW. | TNSLDC/TANTRANSCO to take up with TNPGCL/TNGEPl for participation | TNSLDC/TANTRANSCO |  | Pending | Pending
143/I/9 | Complete Outage of 400kV Ennore SEZ of TNPGCL | 09-05-2026 09:24 | As per the reports submitted, the triggering incident was R-G fault in 400KV-ENNORE SEZ-SUNGAVARACHATRAM-1 at 09:24hrs, B-G fault in 400KV-ENNORE SEZ-NCTPS_STAGE_II-1 at 12:13hrs and the lines tripped. Tripping of both lines led to complete outage of 400kV Ennore SEZ of TNPGCL | TNPGCL to submit detailed report for the event. | TNPGCL |  | Pending | Pending
143/I/9 | Complete Outage of 400kV Ennore SEZ of TNPGCL | 09-05-2026 09:24 | As per the reports submitted, the triggering incident was R-G fault in 400KV-ENNORE SEZ-SUNGAVARACHATRAM-1 at 09:24hrs, B-G fault in 400KV-ENNORE SEZ-NCTPS_STAGE_II-1 at 12:13hrs and the lines tripped. Tripping of both lines led to complete outage of 400kV Ennore SEZ of TNPGCL | TNSLDC/TANTRANSCO to ensure participation from TNPGCL/TNGEPL . | TNSLDC/TANTRANSCO |  | Pending | Pending
143/I/10 | Complete Outage of 400kV UPCL Generating station of Adani, Tripping of 220kV Bus-1 of 220kV Kemar SS and Complete Outage of 220kV MSEZ SS, 220kV Kemar SS and 220kV Kavoor SS of KTPCL | 09-05-2026 17:33 | During antecedent conditions, 400kV UPCL Hebbanahalli Line-1&2 were under outage. As per the reports submitted, the triggering incident was R-G fault in 220kV UPCL Kemar Line-2 and 220kV UPCL Kemar Line-1 and the lines tripped. Tripping of both lines led to complete outage of UPCL Generating station. Subsequently, 220kV Bus coupler at 220kV Kemar SS tripped on over loading which led to tripping of 220kV Bus-1 of 220kV Kemar SS and complete Outage of 220kV MSEZ SS, 220kV Kemar SS and 220kV Kavoor SS | KAR SLDC to take proactive steps as per SOP | KAR SLDC |  | Pending | Pending
143/I/10 | Complete Outage of 400kV UPCL Generating station of Adani, Tripping of 220kV Bus-1 of 220kV Kemar SS and Complete Outage of 220kV MSEZ SS, 220kV Kemar SS and 220kV Kavoor SS of KTPCL | 09-05-2026 17:33 | During antecedent conditions, 400kV UPCL Hebbanahalli Line-1&2 were under outage. As per the reports submitted, the triggering incident was R-G fault in 220kV UPCL Kemar Line-2 and 220kV UPCL Kemar Line-1 and the lines tripped. Tripping of both lines led to complete outage of UPCL Generating station. Subsequently, 220kV Bus coupler at 220kV Kemar SS tripped on over loading which led to tripping of 220kV Bus-1 of 220kV Kemar SS and complete Outage of 220kV MSEZ SS, 220kV Kemar SS and 220kV Kavoor SS | KPTCL to review the Current and Time delay settings for I>3 logic for TOR. KPTCL to take proactive steps as per SOP | KPTCL |  | Pending | Pending
143/I/14 | Compete Outage of 220KV-TP SAURYA LIMITED | 16-05-2026 21:20 | As per the reports submitted, the triggering incident was R-G fault in 220kV 220KV-TP SAURYA LIMITED-KOPPAL-1 and the line tripped. Tripping of the only connected line led to complete outage of 220KV-TP SAURYA LIMITED | Indigrid to enable AR at Koppal End. Indigrid advised to submit the DR/EL as per the IEGC section 37.2 (c) and CEA grid Standard 15.3 time line. | Indigrid |  | Pending | Pending
143/I/14 | Compete Outage of 220KV-TP SAURYA LIMITED | 16-05-2026 21:20 | As per the reports submitted, the triggering incident was R-G fault in 220kV 220KV-TP SAURYA LIMITED-KOPPAL-1 and the line tripped. Tripping of the only connected line led to complete outage of 220KV-TP SAURYA LIMITED | TATA power advised to submit the DR/EL as per the IEGC section 37.2 (c) and CEA grid Standard 15.3 time line. | TATA power |  | Pending | Pending
143/I/15 | Complete Outage of 220kV Vena_GadagPS | 17-05-2026 16:14 | The triggering incident was RY-G fault in the 220kV Gadag Vena_GadagPS Line-1 and the line tripped. Tripping of the only connected line led to complete outage of 220kV Vena_GadagPS. | GTL advised to submit the DR/EL as per the IEGC section 37.2 (c) & CEA grid Standard 15.3 timeline | GTL |  | Pending | Pending
143/I/15 | Complete Outage of 220kV Vena_GadagPS | 17-05-2026 16:14 | The triggering incident was RY-G fault in the 220kV Gadag Vena_GadagPS Line-1 and the line tripped. Tripping of the only connected line led to complete outage of 220kV Vena_GadagPS. | VEENA energy to restore the Veena GTL line at earliest. Veena Energy advised to submit the DR/EL as per the IEGC section 37.2 (c) & CEA grid Standard 15.3 timeline | Veena Energy |  | Pending | Pending
143/I/19 | Complete Outage of 765kV NCPS Pooling station of TANTRANSCO and 765kV NCTPS Generating station of TNPGCL | 18-05-2026 23:30 | 765kV NCPS Pooling station and 765kV NCTPS Generating station are radially connected through 765kV Ariyalur NCPS Line-1&2. During antecedent conditions, 765kV Ariyalur NCPS Line-2 was under outage. As per the reports submitted, the triggering incident was R-Y fault in 765kV Ariyalur NCPS Line-1 and the line tripped. Tripping of the only source led to complete outage of 765kV NCPS Pooling station and 765kV NCTPS Generating station | TNPGCL to submit detailed report for the event | TNPGCL |  | Pending | Pending
143/I/19 | Complete Outage of 765kV NCPS Pooling station of TANTRANSCO and 765kV NCTPS Generating station of TNPGCL | 18-05-2026 23:30 | 765kV NCPS Pooling station and 765kV NCTPS Generating station are radially connected through 765kV Ariyalur NCPS Line-1&2. During antecedent conditions, 765kV Ariyalur NCPS Line-2 was under outage. As per the reports submitted, the triggering incident was R-Y fault in 765kV Ariyalur NCPS Line-1 and the line tripped. Tripping of the only source led to complete outage of 765kV NCPS Pooling station and 765kV NCTPS Generating station | TNSLDC/TANTRANSCO to ensure participation from TNPGCL/TNGEL | TNSLDC/TANTRANSCO |  | Pending | Pending
141/VI/10 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 01-03-2026 12:10 | Station at which DR time synchronisation was not observed SRISAILAM_RIGHT_BANK - 220KV | APGENCO to rectify the DR time synchronization issue at SRISAILAM RIGHT BANK - 220KV | APGENCO | PROTECTION.HPC:TGGENCO: 05/05/2026 10:55:52: There is no DR time Synchronization issue at NSHES end. In recent following 3 trippings of the above feeder, we can observe the DR time Synchronization . 1. 13/03/2026 @ 13:32 Hrs 2. 26/03/2026 @ 12:35 Hrs 3. 27/03/2026 @ 11:40 Hrs | Complied | Complied
142/I/12 | Complete Outage of 220kVTadipathri | 10-04-2026 14:56 | During antecedent conditions, 220kV Tadipathri Boyareddypalli line was under LC. 220kV Tadipathri SS was being fed through 132kV network through 132kV Tadipathri Kondapuram and 132kV Gooty RS-Gudipadu-Ankireddypalli-Komali- Tadipatri feeders. As per the reports submitted, at 14:56hrs, 132kV Tadipathri Ankireddypalli line tripped on R-G fault. Subsequently, 132kV Ankireddypalli Gudipadu feeder tripped on non directional over current protection at Ankireddypalli end. Tripping of both sources led to complete otuage of 220kV Tadipathri SS. | APTRANSCO to comply with CEA Safety Regulations w.r.t the TAP connection at 132kV connectivity for Penna Cement. APTRANSCO to provide DR time sync for 132kV Tadipatri and Kondapuram SS. | APTRANSCO | dee2sp:APTRANSCO: 05/06/2026 15:07:30: 1) Informed to the concerned field authorities to verify the feasibility. 2) At Tadipatri end Kondapuram feeder relays were not compatible for GPS time sync. GPS time sync will be arranged by August-26 | Pending | Pending
142/III/5 | 20KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 26-03-2026 12:35 | As per the reports submitted the triggering incident was high resistance R-G fault in the line (based on the DR, it can be observed from R/X plot that the fault angle at Srisailam end is around 0 degrees and at Nagarjuna Sagar end the fault angle is around 13 degrees). From both the ends, DEF operated and 3 ph tripped. | APGENCO to review the Non configuration of DT for DEF.APGENCO to review the Time Synch issue at NagarjunaSagar RB APGENCO to submit the detailed report on the incident | APGENCO |  | Pending | Pending
142/III/6 | 00kV-KRISHNAPATNAM-SEIL_P2-1 | 28-03-2026 17:23 | In the antecedent condition, 409 Main CB which is connected to Bus-2 was under LC and the line was only connected through 408 Tie Breaker. As per the reports submitted, the triggering incident is the opening of Y-pole breaker without any fault in 400 kV-KRISHNAPATNAM-SEIL_P2-1 only at KRISHNAPATNAM end. After which Pole discrepancy operated after around 7.5 seconds leading to the tripping of R and B poles. This led to the 3ph tripping at KRISHNAPATNAM end. The line was holding at SEIL_P2 end. | APGENCO to review the tripping of Y-ph pole without any fault. APGENCO to review Pole Discrepancy timer at 400KV-KRISHNAPATNAM APGENCO to review the Time Synch issue at Krishnapatnam APGENCO to submit the detailed report on the incident. | APGENCO |  | Pending | Pending
142/III/8 | 400KV-KALPAKKA-ASUPAKA-1 | 03-04-2026 12:03 | As per the reports submitted, the triggering incident was B-G fault in the line. At Asupaka end, the fault was sensed in zone-1 and B-pole opened. After around 1000ms, A/R operated and the fault was sensed again in zone-1 and line tripped on persistent fault with no delay. At KALPAKKA end, the fault was sensed in carrier aided zone-2 and B-pole opened. After around 1200ms, A/R operated and the fault was sensed in zone-2 and the line tripped with a delay of 560ms | APTRANSCO to submit the detailed OEM report on the AR operation at Kalpakka | APTRANSCO | dee2sp:APTRANSCO: 03/06/2026 12:48:21: As per the recommendations of OEM(M/s, Siemens), in BCU AR settings , Cycle-1 action time adopted as 0.2 sec ( earlier it was 0.25 sec) and dead time after evolve fault modified as 1.0 sec ( earlier it was 1.2 sec). After adopting the above settings AR function was tested and found that dead time is 1.0 sec (found OK). | Pending | Pending
142/VI/11 | 220KV-SRISAILAM_RIGHT_BANK-DINDI-1 | 26-03-2026 12:17 | DR Time Synchronization issue at SRISAILAM_RIGHT_BANK - 220KV | APGENCO to rectify the DR Time Synchronization issue at SRISAILAM_RIGHT_BANK - 220KV | APGENCO |  | Pending | Pending
142/VI/47 | 220KV-KOTHAGUDEM_TPS-TIRUVURU-1 | 20-04-2026 15:04 | DR Time Synchronization issue at TIRUVURU - 220KV | APTRANSCO to rectify the DR Time Synchronization issue at TIRUVURU - 220KV | APGENCO |  | Pending | Pending
143/II/1 | Tripping of 220kV Bus-2 of Chilakallu of APTRANSCO | 30-04-2026 13:16 | The triggering incident is the B-G fault in 220KV-CHILLAKALLU-PULICHINTALA-1, during which B-ph breaker failed to open at CHILLAKALLU end and led to the LBB operation in Bus-2 and all elements connected to Bus-2 at CHILLAKALLU tripped and led to the Tripping of 220kV Bus-2 of Chilakallu of APTRANSCO | APTRANSCO to review the DR time synchronization at 220kV Pulichintala and 220kV Chillakallu. APTRANSCO advised to carry out the periodic maintenance of the Breakers | APTRANSCO |  | Pending | Pending
143/II/2 | Tripping of 220kV Bus-1 of 400kV/220kv Jammalamadugu SS | 18-05-2026 18:40 | As per the reports submitted, the triggering incident was B-G fault in 220kV Bus-1. Immediately, 220kV Bus-1 BBP operated and all elements connected to the 220kV Jammalamadugu Bus-1 tripped. | APTRANSCO to review the distance relay settings and furnish the report regarding non sensing of distance protection during the event in 132kV Jammalamadugu Gandikota 2 line. APTRANSCO to verify the PU wiring scheme at Jammalamadugu SS | APTRANSCO |  | Pending | Pending
143/III/1 | 220KV-ASUPAKA-LOWER_SILERU-1 | 21-04-2026 13:37 | As per reports submitted, the triggering incident was high impedance R-G fault (fault angle of around 40 degrees from Lower Sileru end) in the line. At ASUPAKA end, the fault was sensed in Z1 at a distance 42.2 km and carrier was sent, A/R operated the line tripped to persistent fault. At LOWER_SILERU end, the fault was sensed in Z2 but carrier was not received and Z2 time tripped after around 350ms. | APGENCO to configure the Disturbance Recorder (DR) settings of the Main2 relay at Lower Sileru in accordance with the recommendations of the FOLD Committee. | APGENCO |  | Pending | Pending
143/V/2 | 400KV-VTPS_IV-VIJAYAWADA-1 | 13-05-2026 15:08 | As per the reports submitted, the triggering incident is the PLCC maloperation at VTPS end and DT was received in channel-2 at VTPS end and the line tripped only at VTPS end. | APGENCO to review the tripping of 400KV-VTPS_IV-Vijayawadavline-1 due to PLCC maloperation. | APGENCO |  | Pending | Pending
143/VI/1 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 21-04-2026 14:19 | DR Time Synchronization Issue SRISAILAM_RIGHT_BANK - 220KV | APGENCO to review the DR time Synchronization issue at 220Kv SRISAILAM_RIGHT_BANK | APGENCO |  | Pending | Pending
141/III/9 | 400KV/11.5KV YADADRI TPP-ST-2 | 09-03-2026 00:09 | As per the reports submitted, the triggering incident in the downstream 11kV fault. During the event, LV REF Protection operated and 3ph trip | TGGENCO to submit a detailed report on the incident. | TGGENCO |  | Pending | Pending
141/VI/9 | 220KV-SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1 | 01-03-2026 12:10 | Station at which DR time synchronisation was not observed NAGARJUNASAGAR_TS - 220KV | TGGENCO to rectify the DR time synchronization issue at NAGARJUNASAGAR TS 220KV | TGGENCO |  | Pending | Pending
142/I/13 | Complete Outage of 220kV Upper Jurala of TGGENCO | 14-04-2026 05:32 | 220kV Upper Jurala PH was radially connected through 220kV Upper Jurala-Raichur-1&2. The triggering incident is the BBP maloperation at Upper Jurala leading to the tripping of 220kV Upper Jurala-Raichur-1&2. With the tripping of the only connected lines to the 220kV Upper Jurala led to the complete outage of 220kV Upper Jurala of TGGENCO | TGGENCO to review the CT secondary circuit. Non availability of SCADA SOE at UPPER_JURALA end needs review | TGGENCO |  | Pending | Pending
142/II/6 | Tripping of 400kV Bus-2 at Dichipally of TGTRANSCO | 04-04-2026 22:26 | The triggering incident is the R-G Bus fault in 400 kV Bus-2 due to bus post insulator failure leading to Bus Bar protection Operation and leading to the tripping of 400kV Bus-2 at Dichipally due to inclement weather conditions. 400 kV Dichipally-Nirmal line and 400 kV/220 kV Dichipally ICT-4 got tripped during the event. | TGTRANSCO to review the distance protection settings at Nirmal end. | TGTRANSCO |  | Pending | Pending
143/II/3 | Tripping of 400kV Bus-1 of 400kV Shankarapally SS of TGTRANSCO | 19-05-2026 19:02 | As per the reports submitted, the triggering incident was Y-G fault in 400kV Kethyreddypalli Shankarapalli line-1. At Shankarapalli end, the Y-phase breaker failed to open, LBB operated and all lines connected to the 400kV Bus-1 tripped. | TGTRANSCO to verify the wiring of PU cards in Kethireddypally SS. TGTRANSCO to refer the event to OEM and furnish the report to SRPC and SRLDC. | TGTRANSCO |  | Pending | Pending
143/III/10 | 220KV-RAICHUR_KA-UPPER_JURALA-2 | 26-04-2026 16:22 | As per the reports submitted, the triggering incident was B-G fault in the line. At both ends, the B-G fault was sensed in Z1, B pole opened and after around 250ms Y-G fault occurred in the line and Y pole opened and 3ph tripped at both ends. However, at UPPER JURALA end, after 50ms R, Y CB closed and again 3ph tripped due to Z1 operation. | TGGENCO to refer the incident to OEM and submit the report. TGGENCO to rectify the DR time synchronization issue at 2200Kv Upper Jurala. | TGGENCO |  | Pending | Pending
143/VI/3 | 400KV-BPS-YTPS-1 | 21-04-2026 19:15 | DR Time Synchronization Issues YTPS - 400KV | TGGENCO to review the DR time Synchronization issue at 400KV YTPS | TGGENCO |  | Pending | Pending
143/VI/27 | 400KV-SRISAILAM_LEFT_BANK-SATTENPALLY-1 | 10-05-2026 01:44 | SRISAILAM_LEFT_BANK - 400KV | TGGENCO to review the DR time Synchronization issue at 400Kv SLBHES | TGGENCO |  | Pending | Pending
141/I/2 | Complete outage 220kV GM Navar SS and Tripping of 220kV Bus-2 at 220kV Nandhihal of KPTCL | 28-02-2026 15:03 | 220kV GMNavar is radially connected to 220kV Nandhihal through 220kV GMNavar- Nandhihal-1&2. In the antecedent conditions, 220kV GMNavar- Nandhihal-1&2 was connected to 220kV Bus-2 at Nandhihal. The triggering incident is the Y-ph isolator contact failure in 220kV Nandhihal-Kudgi line-5 which came into vicinity of 220kV Nandhihal-Kudgi line-3 creating a Y-B phase bus fault in 220kV Bus-2 at Nandhihal. This led to the BBP operation and tripping of all the elements connected to 220kV Bus-2 at 220kV Nandhihal and led to the Complete outage 220kV GM Navar SS | KPTCL to review the protection settings at Nandihal SS and submit a report in this regard. | KPTCL | Puspha:KPTCL: 05/05/2026 13:39:14: Corrective measures required are taken up with the developer M/s Siemens Gamesa as the hand over of the substation is under process. Busbar protection setting will be taken up jointly. | Pending | Pending
141/I/3 | Complete outage of 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2, and Bus-1 & Bus-2 at Kalburgi of KPTCL | 03-03-2026 11:00 | In the antecedent conditions, multiple bus splits were carried out in the vicinity of 400/220 kV Kalburgi substation to facilitate evacuation of RE power. The triggering incident was the tripping of 400/220kV ICT-1 and 2 at Kalburgi substation. Since multiple substations evacuate power through Kalburgi, the tripping of the evacuation path led to the complete outage of 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2, and Bus-1 & Bus-2 at Ferozabad (Kalburgi) of KPTCL. | 1.KPTCL to submit the report on LVRT compliance during the event. 2.KPTCL to review ICT over current settings at Kalaburgi SS. 3.KPTCL to install PMU at Kalaburgi SS. | KPTCL | Puspha:KPTCL: 05/05/2026 13:36:59: 1. Letter is adressed to CEE, Operations, Kalaburgi and all concerned regarding preventive measures required to prevent re occurrence of such incident , conformation regarding LVRT will be collected from the field. 2 Presently ICT Over current settings are set at 110% ., For further review of the same SPS is to be implemented at 110 % loading. Operation studies required for the design of SPS is under process. 3. The matter is taken up with management for approval. Technical specifications for PMU will be finalized taking technical support from Powergrid. | Pending | Pending
141/I/4 | Complete Outage of 220kV Nagamangala, Anchepalya and Magadi SS of KPTCL | 05-03-2026 13:48 | 220kV Nagamangala SS, 220kV Anchepalya SS, and 220kV Magadi SS are being radially fed from the 220kV Nelamangala Anchepalya line and the 220kV Nelamangala Magadi line. The triggering incident was a B-G fault in the 220kV Nelamangala Anchepalya line and the line tripped and after which 220kV Nelamangala Magadi line tripped on over current protection. WIth the tripping of 220kV Nelamangala Anchepalya and 220kV Nelamangala Magadi line led to the Complete Outage of 220kV Nagamangala, Anchepalya and Magadi SS of KPTCL | 1.KPTCL to disable Over current logic for 220kV lines at Neelamangala , Anchenpalya SS. 2.KPTCL to verify the Over current relay rest settings at Neelamangala , Anchenpalya SS. | KPTCL | Puspha:KPTCL: 05/05/2026 13:29:49: 1. At Nelamangala, OCR has been disabled for 220kV Anchepalya and Magadi lines. 2. At the time of tripping OCR with setting 800Amp setting was in enabled condition, OCR disabled subsequently. | Complied | Complied
141/II/3 | Tripping of 400kV Bus-2 at RTPS of KPCL | 24-02-2026 04:27 | The triggering incident is the B-G bus fault in 400kV Bus-2 at RTPS. All the main breakers connected to Bus-2 got tripped and led to the tripping of 400kV Bus-2 at RTPS. 400kV RTPS-Munirabad was only in service with the main breaker connected to Bus-2 and due to the tripping of the Bus-2 led to the tripping of 400kV RTPS-Munirabad line. All other elements were in service through 400kV Bus-1. | KPCL to measure IR testing of BPI periodically. | KPCL | EE (E )/CEED:KPCL: 05/05/2026 12:14:38: Conductiong IR tests of BPI will be taken up subject to bus shutdown availibility. EE (E )/CEED:KPCL: 06/06/2026 10:02:04: Conductiong IR tests of BPI will be taken up subject to bus shutdown availibility. | Pending | Pending
141/III/5 | 400KV-DONI-GUTTUR-1 | 01-03-2026 14:50 | The triggering incident is the tripping of the line only at GUTTUR end due to suspected DC earth fault. The line was holding at DONI end. | KPTCL to review the Healthiness of control cables at both 400kV Doni and Guttur SS. | KPTCL | Puspha:KPTCL: 05/05/2026 14:48:58: At the time DC grounding issue was there in the substation. The same was rectified. Healthiness of control cables in Doni bay is verified. No abnormalities found | Complied | Complied
141/VI/4 | 400KV-KAIGA-GUTTUR-2 | 24-02-2026 15:45 | Station at which DR time synchronisation was not observed : GUTTUR - 400KV | KPTCL to rectify the DR time synchronization issue at GUTTUR 400 KV | KPTCL | Puspha:KPTCL: 05/05/2026 14:47:50: GOS time sync issue at Guttur has been resolved. Except few old version relays having limitations, all other relays synchronized with GPS clock. | Complied | Complied
142/I/3 | Complete Outage of 400kV YTPS Generating Station of KPCL, 400kV Kalaburagi SS, 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2 of KPTCL | 17-03-2026 21:52 | 400kV YTPS Generating Station, 400kV Kalaburagi SS, 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur ,220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2 are being radially connected through 400kV BPS YTPS Line-1&2. As per the reports submitted, 400kV BPS YTPS Line-1 tripped on R-G fault at 20:27hrs and 400kV BPS YTPS Line-2 tripped on RY fault at 22:26hrs. Tripping of both lines led to complete outage of all radial connected stations. | KPTCL to formulate SOP to manage the YTPS generation and grid upon tripping of single YTPS-BPS line. Time synch issues to be rectified at various stations and compliance report to be furnished. ER, DL & TAR for many 220 kV stations not furnished. KPTCL to take up with concerned entitites and copy of the same shall be furnished. KPCL to submit feedback to KPTCL (Planning) to ensure reliable evacuation. | KPTCL | Puspha:KPTCL: 07/06/2026 15:43:09: The matter was referred to SLDC . It is informed that, in case of tripping of any one line of 400kV BPS-YTPS D/c. action is being to back down UPCL generation and to close bus couplers at Sedam and Shahapur.. Directions have been given to kalaburgi and BPS 400kV SS to contact SLDC immidiately for tripping of any one line between BPS-YTPS and YTPS-Kalaburgi | Pending | Pending
142/II/2 | Tripping of 400kV Bus-1 of 400kV Kalaburagi SS | 18-03-2026 07:51 | As per the reports submitted, while opening the bus reactor 400kV Bus-1 of Kalaburagi got tripped tripping all elements connected to the 400kV Bus-1 | KPTCL to follow SOP during testing and maintanance activities | KPTCL | Puspha:KPTCL: 07/06/2026 15:43:09: Necessary directions have been given to the Substation | Complied | Complied
142/III/12 | Multiple trippings at BPS | 13-04-2026 15:52 | As per the reports submitted, the triggering incident Y-G fault in BPS-YTPS_1 line. At YTPS end the fault was sensed in Zone 2 and at BPS end the fault was sensed in Zone 1. A/R didn't operate from both the ends. At YTPS end 3 phase tripping was observed and at BPS end upon receiving the DT 3 phase tripping was observed. After tripping of YTPS-BPS-1 line at JSW end of JINDAL-BPS-4 line the fault was sensed in Zone 3 but no master trip was initiated. Line got tripped at Jindal end due to suspected Ground Potential Rise. JINDAL-BPS-4 line was holding from BPS. | KPCL to rectify the PLCC issues at the YTPS. | KPCL | EE (E )/CEED:KPCL: 06/06/2026 10:02:04: PLCC is in healthy condition and signal during AR will be checked in co ordinbation with KPTCL | Pending | Pending
142/VI/4 | 220KV-RAICHUR_KA-UPPER_JURALA-2 | 18-03-2026 23:11 | DR Time Synchronization issue at RAICHUR_KA - 220KV | KPCL to rectify the DR Time Synchronization issue at RAICHUR_KA - 220KV | KPCL | EE (E )/CEED:KPCL: 06/06/2026 10:02:04: This line Doesnot connect to KPCL statin, kindly modify to KPTCL | Pending | Pending
142/VI/10 | 220KV-AMBEWADI-PONDA-2 | 25-03-2026 21:20 | DR Time Synchronization issue at AMBEWADI - 220KV | KPTCL to rectify the DR Time Synchronization issue at AMBEWADI - 220KV | KPTCL |  | Pending | Pending
142/VI/20 | 400KV-DONI-GUTTUR-1 | 03-04-2026 12:20 | DR Time Synchronization issue at GUTTUR - 400KV | KPTCL to rectify the DR Time Synchronization issue at GUTTUR - 400KV | KPTCL | Puspha:KPTCL: 07/06/2026 15:46:39: GPS time synchronisation is working at Guttur except few relays. | Pending | Pending
142/VI/30 | 400KV-KALABURAGI-YTPS-2 | 10-04-2026 15:25 | DR Time Synchronization issue at KALABURAGI - 400KV | KPTCL to rectify the DR Time Synchronization issue at KALABURAGI - 400KV | KPTCL | Puspha:KPTCL: 07/06/2026 15:45:18: GPS is in working condition at Kalaburgi 400kV SS, all relays are time synchronised with GPS clock | Complied | Complied
143/III/7 | 220KV-CHIKKODI-TALANGADE | 23-04-2026 22:10 | As per the reports submitted,220Kv Chikkodi Talangade was idle charged from Chikkodi end and the triggering incident was B-G fault in the line. At Chikkodi end the fault was sensed in zone-1 and AR operated. During AR operation, the fault was sensed in Z1 but the breaker did not open and tripped only after 400ms. | KPTCL to rectify the DR time synchronization issue at 220Kv Chikodi. | KPTCL |  | Pending | Pending
143/III/14 | Multiple tripping at 400Kv Jindal TPS | 29-04-2026 00:12 | As per the reports submitted, the triggering incident was R-G fault in 400KV-BPS-JAGALUR-2. At BPS end, the fault was sensed in zone-1. At both ends, A/R operated and the line was holding. At the same time, 400KV-JINDAL-BPS-3 &4 tripped only at Jindal end on suspected rise in Ground potential rise (GPR). | KPTCL to review the non-availability of DR at 400Kv Jagalur during the incident | KPTCL |  | Pending | Pending
143/VI/4 | 220KV-RAICHUR_KA-UPPER_JURALA-2 | 21-04-2026 20:52 | DR Time Synchronization Issue RAICHUR_KA - 220KV | KPTCL to review the DR time Synchronization issue at 220Kv Raichur | KPTCL |  | Pending | Pending
143/VI/11 | 400KV-KOLAR_AC-HOODY-2 | 29-04-2026 20:07 | DR Time Synchronization Issues HOODY - 400KV | KPTCL to review the DR time Synchronization issue at 400Kv Hoody | KPTCL |  | Pending | Pending
143/VI/29 | 400KV-GUTTUR-BTPS-1 | 12-05-2026 16:54 | DR time Synchronization issue at 400Kv Guttur | KPTCL to review the DR time Synchronization issue at 400Kv Guttur | KPTCL |  | Pending | Pending
143/VI/34 | 220KV-AMBEWADI-PONDA-2 | 17-05-2026 20:09 | DR time Synchronization issue at 220Kv Ambewadi | KPTCL to review the DR time Synchronization issue at 220Kv Ambewadi | KPTCL |  | Pending | Pending
142/I/14 | Complete Outage of 220kV Pallom SS and 220kV New Pallom SS of KSEB | 14-04-2026 16:40 | As per the reports submitted, the triggering incident was B-G bus fault on 220kV Bus-2 of 220kV New Pallom station within the bus protection zone of 220kV Pallom - New Pallom line. However, 220kV Bus-2 BBP did not operate at 220kV New Pallom SS and the fault was continuously being fed through 220kV lines connected to 220kV Pallom SS and 220kV New Pallom SS. Eventually these 220kV lines tripped on zone-2 protection at the remote ends and this led to complete outage of 220kV Pallom SS and 220kV New Pallom SS | KSEBL to rectify DR Time sync issue at New Pallom, Sabaragiri & Idduki end. | KSEBL |  | Pending | Pending
142/II/3 | Tripping of 220kV Bus-2 at Idduku PH of KSEB | 18-03-2026 15:26 | As per the reports submitted, the triggering incident was B-G fault in 220kV Bus-2 of Idukki PH. Immediately, 220kV Bus-2 BBP operated and all elements connected to the Bus-2 tripped. | KSEBL to report equipment failure to CEA. | KSEBL |  | Pending | Pending
142/VI/35 | 220KV-PALLOM-NEW PALLOM-1 | 14-04-2026 16:40 | DR Time Synchronization issue at NEW PALLOM - 220KV | KSEB to rectify the DR Time Synchronization issue at NEW PALLOM - 220KV | KSEBL |  | Pending | Pending
142/VI/36 | 220KV-PALLOM-NEW PALLOM-1 | 14-04-2026 16:40 | DR Time Synchronization issue at NEW PALLOM - 220KV | KSEB to rectify the DR Time Synchronization issue at NEW PALLOM - 220KV | KSEBL |  | Pending | Pending
142/VI/36 | 220KV-SABARIGIRI-PALLOM-1 | 14-04-2026 16:40 | DR Time Synchronization issue at SABARIGIRI - 220KV | KSEB to rectify the DR Time Synchronization issue at SABARIGIRI - 220KV | KSEBL |  | Pending | Pending
142/VI/38 | 220KV-IDDUKI-NEW PALLOM-1 | 14-04-2026 16:40 | DR Time Synchronization issue at IDDUKI - 220KV | KSEB to rectify the DR Time Synchronization issue at IDDUKI - 220KV | KSEBL |  | Pending | Pending
143/I/17 | Complete Outage of 220kV Ambalathara SS, 220kV Thalassery SS, 220kV Orkattery SS, 220kV Kanhirode SS, 220kV Mylatty SS of KSEB | 17-05-2026 18:28 | As per the reports submitted, the triggering incident was RBG fault in 220kV Areakode Kanhirode line and RBG fault in 220kV Areakode Orkattery line and both lines tripped. Tripping of both lines led to complete outage of 220kV Ambalathara SS, 220kV Thalassery SS, 220kV Orkattery SS, 220kV Kanhirode SS, 220kV Mylatty SS | KSEBL to check the three phase AR dead time settings in entire KSEBL network. KSEBL to review the DR time synchronization at 220kV Orkkattery and 220kV Kanhirode | KSEBL |  | Pending | Pending
141/II/2 | Tripping of 230kV Bus-2 of 230kV Kayathar SS of TANTRANSCO | 22-02-2026 12:48 | 230kV Kayathar SS is operating with double bus with bus coupler at 230kV level but all elements were connected to 230kV Bus-2. As per the reports submitted, the triggering incident was 230kV YB fault in 230kV Bus-2. Hence 230kV BBP operated and all elements connected in Bus-2 got tripped. 110kV side was in service during the event. | 1.TANTRANSCO to do periodic thermo vision scanning of Kayathar SS Switchyard. 2.TANTRANSCO to implement double bus operation at Kayathar SS. | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:45:23: 1.Informed to System operation wing. 2. cepc:TANTRANSCO: 04/05/2026 17:14:00: 2.Protection clearance issued for implementation of double bus operation. cepc:TANTRANSCO: 05/06/2026 14:00:09: 1. Informed to System operation wing. 2. Regarding implementation of double bus operation, Protection arrangements are provided. System Operation has to implement the double Bus operation.The same is also informed and requested to ensure double bus operation. | Pending | Pending
141/III/4 | 400KV-MANALI-PULIYANTHOPE-2 | 28-02-2026 06:15 | As per the reports submitted, the triggering incident is the B-G fault in the line. At Pulianthope end, the fault was sensed in Line Differential Protection, AR operated and tripped due to persistent fault. At Manali end, the fault was sensed in LDP and B pole openend. After around 1 sec AR operated at remote end intertrip and 3 ph tripped, but even after which AR operated after around 200ms and tripped due to persistent fault. | 1.TANTRANSCO to review the AR attempt after inter trip at Manali end. 2.TANTRANSCO to rectify the DR time synchronization issue at PULIYANTHOPE SS 3.TANTRANSCO to review the Non-availability of SCADA SOE at PULIYANTHOPE | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:35:01: 1. As per scheme, TC1 & TC2 couldn't get trip pulse from 86 lockout relay since 52a contact already open. Hence this happened 2.Pulianthope SCADA SOE checked & Now reported cepc:TANTRANSCO: 05/06/2026 14:00:09: 1. As per logic the sequence is found in order.Complied 2. Complied | Pending | Pending
141/IV/1 | 400KV-NCTPS_STAGE_II-SUNGAVARACHATRAM-1 | 22-02-2026 05:58 | As per the reports submitted, the triggering incident is the B-G fault due to insulator flashover at location 101 from NCTPS ST2 and OPGW cut during the event. At both ends the fault was sensed in Z1 and AR did not operate due to carrier fail. | 1.TNPGCL to review the Non availability of SCADA SOE at NCTPS ST2.2. TNPGCL to review Non operation of AR at NCTPS ST2. | TNPGCL |  | Pending | Pending
141/IV/3 | 220KV-SULURPET-GUMMIDIPOONDI-1 | 27-02-2026 11:39 | As per the reports submitted, the triggering incident is the Y-G fault due to tree clearance issue in the vicinity of the line. At Sullurpet end, the fault was sensed in Z1, AR is disabled and 3ph tripped. At Gummidipundi end, the fault was sensed in Z1, and AR did not operate and 3ph tripped. | 1TANTRANSCO to enable the Auto Reclosure at Sullurpet. 2.TANTRANSCO to review the relay coordination at Gummidipoondi SS, as the phase to ground fault was sensed as phase to phase fault. | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:26:36: AR scheme is healthy in sulurpet feeder. From the DR, It is observed that for a single line to fault in Y phase but R phase current magnitude also around 0.8kA and phase angle is matched with Y & N hence relay may be sensed the fault as line to line fault & issued the three phase trip. On 01.03.2026 at 13:43hrs for a single line to ground fault in B phase AR found successful. | Complied | Complied
141/IV/4 | 765KV-THIRUVALAM-ARIYALUR-1 | 27-02-2026 18:20 | As per the reports submitted, the triggering incident is the Y-G fault in the line. At ARIYALUR, the fault was sensed in Z1, AR operated and was successful and the line was holding. At THIRUVALAM end, the fault was sensed in Z1, AR did not operate in both main and tie and 3ph tripped. | TANTRANSCO to review the Auto Reclosure operation in 765KV-THIRUVALAM-ARIYALUR-1 line at Thiruvalam end. | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:26:36: PGCIL maintain the bay cepc:TANTRANSCO: 05/06/2026 14:00:09: Pending with PGCIL | Pending | Pending
141/VI/3 | 400KV-NCTPS_STAGE_II-MANALI-1 | 24-02-2026 05:01 | Station at which DR time synchronisation was not observed NCTPS_STAGE_II - 400KV | TNPGCL to rectify the DR time synchronization issue at 400kV NCTPS Stage2 | TNPGCL |  | Pending | Pending
141/VI/8 | 400KV-SRIPERUMBADUR-CHITTOOR-1 | 01-03-2026 11:24 | Station at which DR time synchronisation was not observed SRIPERUMBADUR - 400KV | TANTRANSCO to rectify the DR time synchronization issue at SRIPERUMBADUR - 400KV | TANTRANSCO | cepc:TANTRANSCO: 04/05/2026 16:26:36: GPS is available. Time sync will be checked cepc:TANTRANSCO: 05/06/2026 14:00:09: Complied | Pending | Pending
142/I/11 | Complete Outage of 230 kV Arani and Echur of TANTRANSCO | 05-04-2026 23:39 | The triggering incident is the 110kV Y-ph bus PT failure at Arani (as per FIR) causing 110 kV Bus Fault. Without 110kV BBP, the Bus fault was sensed and the lines tripped on Z3 protection operation at remote ends other than 230KV-ARNI-ECHUR-1. 230KV-MAPS-ECHUR-1 line tripped on DEF protection leading to the Complete Outage of 230 kV Arani and Echur of TANTRANSCO | TANTRANSCO to review the remote end Zone3 settings of lines connecting to 230kV Arani SS. TANTRANSCO & NPCIL MAPS to review the distance and DEF coordination and submit report to SRPC & SRLDC. TANTRANSCO to implement 110kV BUSBAR protection at 230kV Arani SS. | TANTRANSCO | cepc:TANTRANSCO: 05/06/2026 14:00:09: Zone.3 setting at Kanchipuram, Singarapet & Echur were restricted to 75% of Transformer equivalent impedance as per TANTRANSCO protection philosophy, Complied As per the discussion , NPCIL has to confirm the revision of definite DEF setting to IDMT pending with NPCIL_ MAPS Action will be taken to implement the 110kV BBP at Arani 230kVSS | Pending | Pending
142/II/1 | Tripping of 230kV TTPS Bus-2 of TNPGCL | 17-03-2026 15:15 | The triggering incident is the Y-G fault in TTPS-Kayathar, where in breaker failed to trip and LBB operated leading to tripping of Bus-2 at TTPS. | TNPGCL to furnish detailed report regarding non sending of DT to KKNPP end during LBB operation. | TNPGCL |  | Pending | Pending
142/VI/5 | 400KV-ALAMATHY-SUNGAVARACHATRAM-1 | 19-03-2026 02:35 | DR Time Synchronization issue at SUNGAVARACHATRAM - 400KV | TANTRANSCO to rectify the DR Time Synchronization issue at SUNGAVARACHATRAM - 400KV | TANTRANSCO | cepc:TANTRANSCO: 05/06/2026 14:00:09: Line clear awaited | Pending | Pending
142/VI/6 | 400KV-ALAMATHY-SUNGAVARACHATRAM-1 | 19-03-2026 02:35 | DR Time Synchronization issue at ALAMATHY - 400KV | TANTRANSCO to rectify the DR Time Synchronization issue at ALAMATHY - 400KV | TANTRANSCO | cepc:TANTRANSCO: 05/06/2026 14:00:09: Line clear awaited | Pending | Pending
142/VI/12 | KARAIKUDI(TN) - 230KV | 26-03-2026 17:57 | DR Time Synchronization issue at KARAIKUDI(TN) - 230KV | TANTRANSCO to rectify the DR Time Synchronization issue at KARAIKUDI(TN) - 230KV | TANTRANSCO | cepc:TANTRANSCO: 05/06/2026 14:00:09: Checked Relay sync with GPS. | Pending | Pending
142/VI/26 | 230KV-ARNI-SINGARPET | 05-04-2026 23:39 | DR Time Synchronization issue at SINGARPET - 230KV | TANTRANSCO to rectify the DR Time Synchronization issue at SINGARPET - 230KV | TANTRANSCO | cepc:TANTRANSCO: 05/06/2026 14:02:14: Checked relay sync with GPS | Pending | Pending
142/VI/41 | 400KV/230KV SRIPERUMBADUR_TN-ICT-3 | 15-04-2026 13:38 | DR Time Synchronization issue at SRIPERUMBADUR_TN - 400KV | TANTRANSCO to rectify the DR Time Synchronization issue at SRIPERUMBADUR_TN - 400KV | TANTRANSCO | cepc:TANTRANSCO: 05/06/2026 14:06:17: SAS C&R cepc:TANTRANSCO: 05/06/2026 14:07:35: Now Non SAS C&R panel available. New SAS C&R panel alloted. Action is being taken to replace the NON SAS panel and recommendation will be complied | Pending | Pending
142/VI/44 | 400KV/230KV PULIYANTHOPE-ICT-1 | 19-04-2026 05:32 | e DR Time Synchronization issue at PULIYANTHOPE - 400KV | TANTRANSCO to rectify the DR Time Synchronization issue at PULIYANTHOPE - 400KV | TANTRANSCO | cepc:TANTRANSCO: 05/06/2026 14:02:14: Checked relay sync with GPS | Pending | Pending
143/I/8 | Complete Outage of 230kV NCTPS Generating station, 230kV Kilpauk SS, 230kV Ganesh Nagar SS, 230kV Basin Bridge SS, 230kV Athipatu SS of TANTRANSCO | 08-05-2026 03:30 | As per the reports submitted, the triggering incident was Y-G fault in 230kV Basin Bridge Tondiarpet line at 03:29:49hrs. At Tondiarpet end, the fault was sensed in zone-1 and the line tripped as A/R lockout operated. At Basin Bridge end, the fault was sensed in zone-1 and Y-pole opened. A/R operated and YB fault is observed after Auto reclosure. However, the fault was not sensed at Basin Bride end. The fault was being continuously fed by 230kV Basin bridge connected lines and other source feeders on zone-3 protection. Subsequently, at 03:30hrs, Y-G fault was observed in 230kV NCTPS Sriperumbudur line. At both ends, the fault was sensed in zone-1. At NCTPS end, A/R did not operate and the line tripped. At Sriperumbudur end, Y-pole opened. B-G fault was sensed in A/R dead time and the line tripped. Tripping of all source feeders led to complete outage of 230kV NCTPS Generating station and all radial connected stations which are 230kV Kilpauk SS, 230kV Ganesh Nagar SS, 230kV Basin Bridge SS, 230kV Athipatu SS. | TANTRANSCO to enable AR for basinbridge line at Tondiarpet TANTRANSCO to do regular thermovision scanning of switchyard to identify hotspots in jumpers. TANTRANSCO to transplay the event and furnsih the report to SRPC & SRLDC. TANTRANSCO to review the distance settings at Basin Bridge end. TANTRANSCO to ensure both Main-1&2 relays to be LDP for lines less than 10km. | TANTRANSCO |  | Pending | Pending
143/III/8 | 420KV/21KV NCTPS_STAGE_II-GT-5 | 26-04-2026 08:11 | As per the report submitted, the triggering incident is the tripping of 420KV/21KV NCTPS_STAGE_II-GT-5 due to maloperation of Pre-Sync Earth Fault relay. | TNPGCL is advised to submit the detailed report on the incident. | TNPGCL |  | Pending | Pending
143/III/27 | 400KV-NCTPS_STAGE_II-MANALI-1 | 12-05-2026 01:42 | As per the reports submitted, line got tripped due to human error at MANALI end, DC supply was disturbed hence GD stage-3 trip operated in NCTPS bay & DT extended to remote end. Both M1 and M2 relays of NCTPs-II received Direct Trip (DT) indications from the Manali end through both communication channels, resulting in feeder tripping via operation of 86A and 86B lockout relays. | TANTRANSCO to strictly adhere to the approved Standard Operating Procedures (SOPs) while restoring AC supply and operating AC MCBs | TANTRANSCO |  | Pending | Pending
143/IV/6 | 400KV-OTTAPIDARAM-THENNAMPATTY-1 | 9-04-2026 13:50 | As per the reports submitted, the triggering incident was R-G fault in the line. At OTTAPIDARAM end, the fault was sensed in Z1, R pole opened and then after 30ms 3ph tripped. At THENNAMPATTY end, the fault was sensed in Z1 and AR did not operate | TANTRANSCO to review the A/R operation of A/R at Ottapidaram end and Thennampatty end | TANTRANSCO |  | Pending | Pending
143/IV/ | 400KV-KARAIKUDI-KAMUDHI-1 | 02-05-2026 20:38 | As per the reports submitted, the triggering incident was R-G fault in the line. At KARAIKUDI end, the fault was sensed in carrier aided Z2 at a distance of 118km, R pole opened, A/R operated and was successful and line was holding. At KAMUDHI end, the fault was sensed in Z1 at a distance of 13km, A/R did not operate and the line tripped. | TANTRANSCO to review the A/R operation of A/R at 400Kv Kamudhi | TANTRANSCO |  | Pending | Pending
143/IV/ | 400KV-ARIYALUR-PUGALUR-1 | 05-05-2026 19:02 | As per the reports submitted, the triggering incident was R-G fault in the line. At ARIYALUR end, the fault was sensed in Z1 at a distance of 2.1km, R pole opened, A/R did not operate and other 2 poles tripped during A/R dead time. At PUGALUR end, the fault was sensed in carrier aided Z2 at a distance of 283km, R pole opened, A/R operated and was successful and line was holding. Line belongs to TNEB. Earth wire snapping was reported by TNEB and Line was Hand tripped from Karur for restoration works. Line is taken in service. | TANTRANSCO to review the A/R operation of A/R at 400Kv Ariyalur. | TANTRANSCO |  | Pending | Pending
143/VI/2 | 400KV-ENNORE SEZ-SUNGAVARACHATRAM-1 | 21-04-2026 16:36 | DR Time Synchronization Issue SUNGAVARACHATRAM - 400KV | TANTRANSCO to review the DR time Synchronization issue at 400KV SUNGAVARACHATRAM | TANTRANSCO |  | Pending | Pending
143/VI/17 | 400KV-ALAMATHY-TIRUVALAM_TN-1 | 03-05-2026 15:56 | DR time Synchronization issue at 400Kv Alamathy | TANTRANSCO to review the DR time Synchronization issue at 400Kv Alamathy | TANTRANSCO |  | Pending | Pending
143/VI/18 | 400KV-NCTPS_STAGE_II-MANALI-1 | 07-05-2026 06:03 | DR time Synchronization issue at 400Kv NCTPS Stage-II | TNPGCL to review the DR time Synchronization issue at 400Kv NCTPS Stage-II | TNPGCL |  | Pending | Pending
143/VI/21 | 230KV-BASIN_BRIDGE-TONDIARPET-1 | 08-05-2026 03:30 | DR time Synchronization issue at 230Kv Tondiarpet | TANTRANSCO to review the DR time Synchronization issue at 230Kv Tondiarpet | TANTRANSCO |  | Pending | Pending
141/VI/11 | 400KV-KOLAR_AC-SRIPERUMBADUR-1 | 03-03-2026 14:09 | Station at which DR time synchronisation was not observed KOLAR_AC - 400KV | PGCIL SR-II to rectify the DR time synchronization issue at KOLAR AC - 400KV | PGCIL (SR-II) |  | Pending | Pending
142/III/9 | 400KV-DICHPALLY-NIZAMABAD-1 | 04-04-2026 22:31 | During the fault at Nirmal substation due to inclement weather, 400 kV-DICHPALLY-NIZAMABAD-1 line tripped only at NIZAMABAD end. | PGCIL SRI was advised to implement line differential protection with both built-in backup distance protection in main-I and mainII relays in 400KVDICHPALLYNIZAMABAD1. PCSC forum advised PGCIL SRI to comply with the grid code and avoid intentional delay of 100msec for zone1 distance protection. PGCIL SRI to provide the detailed report on the incident. | PGCIL (SR-I) |  | Pending | Pending
142/VI/7 | 220KV-HIRIYUR-ZENATARIS_PSS-1 | 21-03-2026 14:09 | DR Time Synchronization issue at HIRIYUR - 220KV | KPTCL to rectify the DR Time Synchronization issue at HIRIYUR - 220KV | PGCIL (SR-II) | Puspha:KPTCL: 07/06/2026 15:44:17: Zentharis is connected to Hiriyur PGCIL not Hiriyur KA | Pending | Pending
141/I/5 | Complete Outage 220kV Renew_Surya_Koppal of RENEW | 08-03-2026 05:49 | 220kV Renew_Surya_Koppal is connected radially to KOPPAL through 220KV-KOPPAL-Renew_Surya_Koppal-1. The triggering incident is the B-G fault in the 220KV-KOPPAL-Renew_Surya_Koppal-1 line and tripping of the only line connected to 220kV Renew_Surya_Koppal led to the Complete Outage 220kV Renew_Surya_Koppal of RENEW | 1.M/s Renew to submit detailed report for the event. 2.M/s Renew to Enable Auto reclosure for 220kV Koppal Renew Surya line. | M/s Renew |  | Pending | Pending
141/I/6 | Complete outage of 220kV SPRING_PUGALUR of SPRING | 11-03-2026 14:17 | 220kV SPRING_PUGALUR is connected radially to PUGALUR through 230KV-PUGALUR-SPRING_PUGALUR-1. The triggering incident is the B-G fault in the 230KV-PUGALUR-SPRING_PUGALUR-1 line and tripping of the only line connected to 220kV SPRING_PUGALUR led to the Complete outage of 220kV SPRING_PUGALUR of SPRING | Spring Pugalur to submit detailed report regarding non operation of AR in consulattion with OEM. | M/s Spring Pugalur |  | Pending | Pending
141/I/7 | Complete Outage of 220kV TP SAURYA of TATA POWER | 13-03-2026 15:07 | 220kV TP SAURYA is connected radially to KOPPAL through 220KV-TP SAURYA LIMITED-KOPPAL-1. The triggering incident is the B-G fault in the 220KV-TP SAURYA LIMITED-KOPPAL-1 line and tripping of the only line connected to 220kV TP SAURYA led to the Complete Outage of 220kV TP SAURYA of TATA POWER | 1.TATAPOWER to verify healthiness of the jumpers at all tower locations. 2.TATAPOWER to install pilot insulators for angle towers. 3.TATAPOWER to enable AR in coordination with Indigrid. 4.TATAPOWER to follow the IEGC mentioned timeline for furnish FIR, EL & DR to SRLDC | M/s TATAPOWER |  | Pending | Pending
141/III/8 | 220KV/33KV KSPPL-ICT-2 | 08-03-2026 10:24 | As per the reports submitted, the triggering incident is the 33kV downstream fault, during which 220KV/33KV KSPPL-ICT-2 tripped on Earth Fault Protection. | KLEIO Solar IS advised to conduct a detailed inspection of all isolator clamps and associated conductors in the switchyard to identify any loose connections, mechanical wear or deterioration. Necessary corrective actions shall be undertaken. | M/s KLEIO Solar |  | Pending | Pending
141/VI/12 | 400KV/230KV NTPL-ICT-1 | 04-03-2026 16:38 | Station at which DR time synchronisation was not observed NTPL - 400KV | NTPL to rectify the DR time synchronization issue at NTPL - 400KV | NTPL |  | Pending | Pending
141/VI/13 | 400KV-KAIGA-GUTTUR-2 | 13-03-2026 05:27 | Station at which DR time synchronisation was not observed KAIGA - 400KV | NPCIL KAIGA to rectify the DR time synchronization issue at KAIGA - 400KV | NPCIL KAIGA |  | Pending | Pending
142/I/1 | Complete Outage of 220kV Zenataris | 16-03-2026 14:40 | As per the reports submitted, the triggering incident was DC supply failure at 220kV Zenataris leading to the tripping of 220kV Hiriyur Zenataris line. Tripping of the only connected line led to complete outage of 220kV Zenataris. | M/s Zenatrius to disable CTD for lines. M/s Zentarius to strictly adhere to SOP during testing activites. | M/s Zenatrius |  | Pending | Pending
142/I/5 | Complete Outage of 220kV ZENATARIS_PSS | 21-03-2026 14:09 | 220 kV Zenataris_PSS is connected to Hiriyur through 220KV-HIRIYUR-ZENATARIS_PSS-1. As per the reports submitted, the triggering incident was YB fault in 220KV-HIRIYUR-ZENATARIS_PSS-1 and the line tripped. Tripping of the only connected line led to complete outage of ZENATARIS_PSS - 220KV | M/s Zentaris to submit the detailed report of the event, mentioning the reason for non sening of not detecting the fault at the generator end during the event. | M/s Zentaris |  | Pending | Pending
142/I/6 | Complete Outage of 220kV Serentica_RI3PL_Gadag_Solar and 220kV Serentica_RI3PL_Gadag_wind | 23-03-2026 21:58 | As per the reports submitted, the triggering incident was R-G fault in 220 kV-GADAG_PSS-Serentica_RI3PL_Gadag_Solar-1 and the line tripped. Tripping of the only connected line led to complete outage of 220kV Serentica_RI3PL_Gadag_Solar and 220kV Serentica_RI3PL_Gadag_wind | 1. M/s Serentica to furnish EL, DR & TAR. 2. M/s Serentica to submit the detailed report on the incident. | M/s Serentica |  | Pending | Pending
142/I/8 | Complete Outage of 220kV SAEL2 | 29-03-2026 15:52 | The triggering incident was R-G fault in 220 kV-KURNOOL_PG_III-SAEL2-1 and the line tripped. Tripping of the only connected line led to complete outage of 220 kV SAEL2 | SAEL to rectify the DR time sync issues. SAEL to submit the detailed report for DT sending during the event in consultation with OEM. | SAEL |  | Pending | Pending
142/I/9 | Complete Outage of 220kV Renew_Surya_Koppal of RENEW | 30-03-2026 14:11 | As per the reports submitted, the triggering incident was tripping of 220kV Koppal-RSRPL line while charging 220/33kV ICT-2 at 220kV Renew_Surya_Koppal and DT was sent to Koppal end and the line tripped. Tripping of the only connected line led to complete outage of 220kV Renew_Surya_Koppal. | M/S Renew to consult the OEM and submit detailed report regarding sending of DT and tripping of line during the event. | M/S Renew |  | Pending | Pending
142/I/15 | Complete outage of 400kV JSW_Rajapura and JSW_Gowripura of JSW | 16-04-2026 15:18 | 400kV JSW_Rajapura and JSW_Gowripura of JSW is radially connected to Jindal TPS through 400kV Jindal TPS- JSW_Rajapura. The triggering incident is the R-G fault in the multicircuit tower portion in 400kV Jindal-BPS-4 and 400kV JIndal TPS- JSW_Rajapaura and the lines tripped. Due to the tripping of the only connected line to 400kV JSW_Rajapura and JSW_Gowripura led to the complete outage of 400kV JSW_Rajapura and JSW_Gowripura. During the same time 400kV Jindal-BPS-3 tripped due to suspected ground potential rise. | JSW-RE to funish the DR/ EL regarding the event to SRPC & SRLDC. JSWEL to submit the GPR investigation report from M/s Manav. | JSW-RE |  | Pending | Pending
142/IV/5 | 220KVNPKUNTA PSS3 NPKUNTA1 | 13-04-2026 14:02 | As per the reports submitted, the fault triggering incident was BG fault in the line. At NPKUNTA end the fault was sensed in differential protection, AR operated but due to persistent fault 3 phase tripping was observed. At NPKUNTA PSS3 end fault was sensed in differential protection, AR didn't operate and 3 phase tripped for the first fault itself. | APSPCL to review the AR operation at NP Kunta PSS3 end. | APSPCL |  | Pending | Pending
142/VI/1 | TP SAURYA LIMITED - 220KV | 17-03-2026 19:35 | DR Time Synchronization issue at TP SAURYA LIMITED - 220KV | TP SAURYA LIMITED to rectify the DR Time Synchronization issue at TP SAURYA LIMITED - 220KV | M/s TP SAURYA LIMITED |  | Pending | Pending
142/VI/17 | 220KV-KURNOOL_PG_III-SAEL2-1 | 29-03-2026 15:55 | DR Time Synchronization issue at SAEL2 - 220KV | SAEL to rectify the DR Time Synchronization issue at SAEL2 - 220KV | SAEL |  | Pending | Pending
142/VI/49 | 400KV-KAIGA-GUTTUR-2 | 20-04-2026 20:25 | DR Time Synchronization issue at KAIGA - 400KV | NPCIL KAIGA to rectify the DR Time Synchronization issue at KAIGA - 400KV | NPCIL KAIGA |  | Pending | Pending
143/I/2 | Complete Outage of 220kV Green Infra_GadagPS of GIREL | 29-04-2026 04:40 | The 220 kV Green InfraGadag PS station is radially connected to the 220 kV Gadag PSS station. The triggering incident was an RG fault on the line during inclement weather conditions. The line tripped at both ends, resulting in a complete outage of the Green Infra Gadag PS station. | GIREL to refer the non operation of A/R during the event to OEM and submit report in this regard GIREL to rectify the SCADA SOE reporting issues. Gadag to review the A/R operation in 220KV-GADAG_PSS-Green Infra_GadagPS-1 | M/S GIREL |  | Pending | Pending
143/I/3 | Complete Outage of 220kV Vena_GadagPS of Vena Energy | 29-04-2026 05:28 | 220 kV Vena_GadagPS station radially connected with 220 kV Gadag_PSS station through Vena_GadagPS-Gadag_PSS-1 line. The triggering incident was Y-G fault during inclement weather conditions; this led to tripping of the 220kV Vena_GadagPS-Gadag_PSS-1 line. The tripping of only connected line to 220kV Vena_GadagPS led to the complete outage of 220kV Vena_GadagPS. | VEENA Energy to consult OEM regarding AR logic and submit a report. VEENA energy to revise the PD time to 2.5 Seconds. | M/S VEENA Energy |  | Pending | Pending
143/I/6 | Complete Outage of 230kV JSW_Vilanthikulam of JSW_RE | 02-05-2026 18:39 | 230 kV JSW_Vilanthikulam generating station(wind) radially connected 230 kV TTGS station through 230KV-TTGS-JSW_Vilathikulam_300MW-1 line. The triggering incident was R-G fault due to inclement weather. Although A/R operated at both ends, but at TTGS end 3 phase tripping was observed without any fault, and line is holding from JSW_Vilathikulam end. As the line is a radial feeder, the tripping of the line at TTGS station led to complete outage of 230kV JSW_Vilanthikulam station. | JSW-Vilathikulam to rectify the AR issue at TTGS end and submit report to SRPC & SRLDC. | JSW-Vilathikulam |  | Pending | Pending
143/I/11 | Complete Outage of 230kV JSW_Vilanthikulam of JSW_RE | 11-05-2026 09:00 | 230 kV JSW_Vilanthikulam generating station(wind) radially connected 230 kV TTGS station through 230KV-TTGS-JSW_Vilathikulam-1 line. Further all elements were connected to 230kV Bus-2 at JSW_Vilathikulam. The triggering incident was R-Y-B fault due to failure of 33kV bus supporting insulators in the Y and B phases near LV side of PTR. During which the ICT protection operated but the breaker failed to open leading to LBB operation and tripping all the elements connected to Bus-2 including 230KV-TTGS-JSW_Vilathikulam-1 line and DT was sent to remote end. Due to the tripping of the only connected line to JSW_Vilathikulam led to the complete outage of 230kV JSW_Vilanthikulam | JSW-RE to submit detailed report of the event | JSW-RE |  | Pending | Pending
143/I/12 | Complete outage of 220kV Vena_GadagPS | 12-05-2026 10:32 | As per the reports submitted, the triggering incident was the DC supply failure to the 220 kV Vena_Gadag PS plant due to human error during maintenance work of auxiliary services. Immediately, 220kV Gadag_PSS Vena_GadaPS-1 line tripped at Vena end and DT was sent to Gadag end. The line tripped at both ends leading to complete outage of 220kV Vena_GadagPS. | Veena Energy to follow SOP during testing and maintenance activites Vena Energy to review the DC redundancy at 220kV Vena_GadagPS plant Veena Energy to disable CTD for lines. | M/S Veena Energy |  | Pending | Pending
143/I/13 | Complete Outage of 220kV Renew_Surya_Ojas_Koppal_W of Renew | 15-05-2026 05:20 | As per the reports submitted, the triggering incident was R-G fault in 220KV-Renew_Surya_Ojas_Koppal_W-KOPPAL-1 line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Renew_Surya_Ojas_Koppal_W of Renew | M/s Renew to submit detailed report of the event | M/s Renew |  | Pending | Pending
143/I/18 | Complete Outage of 220kV Hiriyur_Ostro | 18-05-2026 21:28 | As per the reports submitted, the triggering incident was R-G fault in 220kV Hiriyur_Ostro Hiriyur line and the line tripped. Tripping of the only connected line led to complete outage of 220kV Hiriyur_Ostro | M/s Ostro Kannada to Implement Auto reclosure for the lines immediately. | M/s Ostro Kannada |  | Pending | Pending
143/III/22 | 400KV-VALLUR-ALAMATHY-1 | 08-05-2026 05:19 | As per the reports submitted, the triggering incident was R-G fault in the line. At Vallur end, the fault was sensed Z1 at a distance of 0.2km, R pole opened and the other 2 phases tripped after around 300ms. 3ph AR operated after around 1s and tripped without any fault. At ALAMATHY end, the fault was sensed in Z1 at a distance of 27.5km, R pole opened, A/R operated and was successful and Line was holding. | NTECL Vallur to submit the detailed report on the incident. | NTECL Vallur |  | Pending | Pending
143/III/24 | 220KV-NP_KUNTA-GALIVVEDU-2 | 08-05-2026 13:51 | As per the reports submitted, the triggering incident is the tripping of 220KV-NP_KUNTA-GALIVVEDU-2 line only at GALIVVEDU end without any relay indications. The line was holding at NP_KUNTA end. | APSPCL to submit the detailed report on the incident | APSPCL |  | Pending | Pending
143/III/25 | Multiple trippings at 400Kv Vallur | 09-05-2026 08:31 | As per the reports submitted, the triggering incident was Y-G fault in 400KV-KALVENDAPATTU-VALLUR-2 line. At KALVENDAPATTU end, the fault was sensed in carrier aided Z2 at a distance of 106km, Y pole opened, A/R operated the line tripped on subsequent fault during A/R dead time due to Conductor snapping in Vallur SS Tower Gantry inside switchyard. At VALLUR end, the fault was sensed in Z1 at a distance of 59km, Y pole opened, A/R operated the line tripped again Subsequent fault during A/R reclaim time. At the same time, at VALLUR end, Line got tripped on DC Earth fault(As per the FIR) and the line was holding at Alamathy end. | NTECL Vallur to submit the detailed report on the incident. | NTECL Vallur |  | Pending | Pending
143/VI/28 | 400KV-KAIGA-GUTTUR-1 | 11-05-2026 16:23 | DR time Synchronization issue at 400Kv Kaiga | NPCIL Kaiga to review the DR time Synchronization issue at 400Kv Kaiga | NPCIL Kaiga |  | Pending | Pending
143/VI/33 | 400KV-MALKARAM-RAMAGUNDAM-1 | 16-05-2026 16:21 | DR time Synchronization issue at 400Kv Ramagundam | NTPC RSTPS to review the DR time Synchronization issue at 400Kv Ramagundam | NTPC RSTPS |  | Pending | Pending