Status of units still operating under Restricted Governor Mode of Operation (RGMO)

| Generating Station | Capacity (MW) | FGMO/ RGMO status | Update |
| --- | --- | --- | --- |
| Nagarjunasagar RCPH | 3 x 30 | RGMO | The present governor system is not capable of FGMO mode. It is possible only after R&M works and R&M works are still under consideration by management. |
| HNPCL | 2 x 520 | RGMO | APSLDC needs to insist on HNPCL to adhere to the IEGC. |
| Raichur TPS | 7 x 210 + 1 x 250 | Partial | Unit 1: After unit restoration Unit 2, 3 & 8: Under FGMO Unit 4: R&M works completed. Logic is ready and will be implemented within a week Unit 5-7: in contact with BHEL for implementation of FGMO and will be taken up along with AOH |
| Yeramarus TPS | 2 x 800 | Partial | Unit 1: FGMO Unit 2: HP control valve and stop valve vibration problem. M/s BHEL and M/s Siemens are working to resolve the issue. After attending the issue, the unit will be put on FGMO. 53rd TCC: BHEL and Siemens are working to resolve the issues. |
| Kadra | 3 x 50 |  | Some issues are being faced in software and tuning of EHGC at both power houses. Presently, in consultation with BHEL. Budgetary provision is made and work order needs to be placed. Expected to be implemented by Oct-Nov 2025 |
| Kodasalli | 3 x 40 |  |  |
| Sharavati | Unit 2: 103.5 MW | Unit 1, 3-10 are in FGMO | Unit 2 have issues with unit processor controller of governor system. The procurement process is under progress. Implementation timeline is dependent on supply of UPC from M/s GE. |
| Supa | 2 x 50 |  | During the R&M works of Supa power house in FY 2024-25. It is proposed to take up replacement of existing EHGC system with new Digital governor and auto sequencer system with RFGMO/FGMO feature. Expected to be completed by March 2026. |
| NCTPP Stage II | 2 x 600 | RGMO | Problems with control system. BHEL had not yet responded. In the meantime, NCTPP II stated that the in-house team is planning try and implement FGMO in consultation with other plants by December-2025. |
| Neyveli STCMS (TAQA) | 1 x 250 |  | TNSLDC had instructed to implement FGMO along with AOH |
| SEPC | 1 x 525 | RGMO | 53rd TCC: TNSLDC informed that SEPC has yet to shift to FGMO mode |
| Valuthur Gas Turbine Power Station (VGTPS) | Phase I: 59.9+35.1 Phase II: 58.5+33.7 |  | TNSLDC stated that implementation of FGMO is not feasible in the current setup. SRLDC also sought technical clarifications regarding how the control system was designed without incorporating governor control. |
| Nagarjunasagar | Unit 1: 110 MW | Unit 2-8: already under FGMO | Unit 1: Capital overhaul is under progress and is expected to be completed in 2 months. Purchase order is placed for governor system with BHEL. Implementation of FGMO will be taken up immediately after capital overhaul. Expected by September 2025. |
| Simhadri STPS Stage I | 2 x 500 | Unit 1-2: RGMO | 53rd TCC: Unit-1: Expected by November 2025. Unit-2: Will be taken up at the earliest opportunity. Although the scheduled shutdown is in December 2026, the activity will be completed earlier as committed in the special meeting. Some DCS modifications are required. |
| Neyveli TS II | 7 x 210 | Unit 4-7: RGMO | Stage 1: implemented Stage 2: Load unsettling issues are persisting due to the mill. Once, it settles down, FGMO implementation will be taken up: |