The status of Units identified under Phase 1 (July 2024 – June 2026)

| Year | Month | Sector | Organisation | Name of Project | Unit No. | Capacit y (MW) | 223rd OCC update |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2024 | November | State | APPDCL | DAMODARAM SANJEEVAIAH TPS | 3 | 800 | 40% TML was achieved. All 3 ramp rates are achieved. |
| 2024 | November | State | TANGEDCO | METTUR TPS-II | 1 | 600 | (update from TN spl meeting on 28.01.2025) TML of 40% and ramp rates of 2% and 3% are achieved. For 40-55% @ 1% ramp, OEM is being consulted (223rd OCC update) Existing ramp rate is 0.75% (4.5 MW/min) |
| 2024 | November | State | TSGENCO | BHADRADRI TPP | 4 | 270 | Test run for 2 hours was conducted. 40% load (270 MW) was achieved on all units with a lot of deviation in parameters. A committee was constituted to study the causation of deviations and suggest remedial measures and further study ramp rates implementation. |
| 2025 | February | State | TSGENCO | BHADRADRI TPP | 3 | 270 |  |
| 2025 | March | State | TSGENCO | BHADRADRI TPP | 2 | 270 |  |
| 2025 | July | State | TSGENCO | BHADRADRI TPP | 1 | 270 |  |
| 2024 | December | Private | HNPC | VIZAG TPP | 2 | 520 | At present operating with TML of 55% Informed that HNPCL was litigation with BHEL (OEM) and so the OEM was not supporting. Exploring options with alternative vendors. |
| 2024 | December | Private | ITPCL | ITPCL TPP | 2 | 600 |  |
| 2024 | December | Central | NTPC | SIMHADRI | 4 | 500 | Generator stated that flame stability problem was arising when generating under 55%, hence were unable to achieve TML of 40 %. (same status as of unit-3 under pilot phase) |
| 2025 | January | Central | NTECL | VALLUR TPP | 1 | 500 | Generator informed that to achieve 40% load, 3 mill operation is required causing issues with flame stability making oil support necessary. NTECL informed that a committee is being formed |
| 2025 | November | Central | NTECL | VALLUR TPP | 2 | 500 |  |
| 2026 | March | Central | NTECL | VALLUR TPP | 3 | 500 |  |
| 2025 | January | State | SCCL | SINGARENI TPP | 1 | 600 | TGSLDC to take an update and action plan from Singareni TPP |
| 2025 | March | State | SCCL | SINGARENI TPP | 2 | 600 |  |
| 2025 | January | Private | SPPL | Thoothukudi St IV | 1 | 525 |  |
| 2025 | February | State | KPCL | BELLARY TPS | 3 | 700 | Testing was held. 40% load and all 3 ramp rates are achieved. It was clarified that testing was done but units are not being operated on a sustained basis MS, SRPC reiterated that flexible operation needs be available on a sustained basis and SLDCs should be able to schedule |
| 2025 | February | Central | NTPC | KUDGI STPP | 1 | 800 | Tried on 2 instances but unit tripped on MS temperature low and flame failure. The generator is working on it. |
| 2025 | December | Central | NTPC | KUDGI STPP | 3 | 800 |  |
| 2026 | March | Central | NTPC | KUDGI STPP | 2 | 800 |  |
| 2025 | March | Private | SEIL | PAINAMPURAM TPP | 2 | 660 | All 4 units tested and identified few issues in operating parameters. 40% is achieved for a short period but not on sustained basis. For ramp up, trails are going on. The issues have been taken up with OEM |
| 2025 | July | Private | SEIL | SGPL TPP | 1 | 660 |  |
| 2026 | January | Private | SEIL | PAINAMPURAM TPP | 1 | 660 |  |
| 2025 | July | Central | NTPL | Thoothukudi (JV) TPP | 2 | 500 | OEM is being consulted and waiting for their reply |
| 2025 | December | Central | NTPL | Thoothukudi (JV) TPP | 1 | 500 |  |
| 2025 | November | State | APPDCL | DAMODARAM SANJEEVAIAH TPS | 2 | 800 | Status of Units 1&2: 40% TML was achieved on multiple occasions. Being a super-critical unit, dry mode of operation was used to operated at 40 % load. Ramp rates of 3% (@70-100%) and 2% (@55-70%) were achieved. For 40-55%, 0.7% ramp was achieved. To achieved 1% ramp, OEM is being consulted and the logic in this regard is also being developed. In consultation with OEM, APPDCL assured that 1% ramp rate will also be achieved. |
| 2026 | February | State | APPDCL | DAMODARAM SANJEEVAIAH TPS | 1 | 800 |  |
| 2025 | November | State | TSGENCO | KOTHAGUDEM TPS (STAGE-7) | 12 | 800 | Management had constituted a committee SRPC requested to start the trial runs and take necessary actions to meet the target by November 2025 |
| 2025 | December | State | TANGEDCO | NORTH CHENNAI TPS | 4 | 600 | (update from TN spl. Meeting on 28.01.2025) 40% TML and all ramp rates are achieved |
| 2026 | January | State | TANGEDCO | NORTH CHENNAI TPS | 5 | 600 |  |
| 2026 | January | State | APGENCO | RAYALASEEMA TPS | 6 | 600 | Trial run for 40% was conducted but couldn’t achieve. OEM is being contacted for 40% TML and 1% ramp rate. TML of 55% and ramp rates of 3% and 2% are achieved |
| 2026 | February | State | KPCL | YERMARUS TPP | 2 | 800 | Commercial offer was received |