    - Andhra Pradesh

- Transmission Constraints with Relieving Measures with Anticipated Timeline – Short Term

  - 400/220kV ICT constraints

| Sl. No | Present Constraints | Action to be taken | Remarks |
| --- | --- | --- | --- |
| 1 | 400/220 kV Kalpakka ICTs (3x315 MVA) | 400/220 kV Kalpakka 4th ICT 500 MVA | It will relieve the overloading of existing ICTs Time line: March-2026 |
| 2 | 400/220 kV kV Kota ICTs (2x315 MVA) | 400/220kV kV Kota 3rd ICT 500 MVA | It will relieve the overloading of existing ICTs Time line: June-2026 |
| 3 | 400/220 kV Rachagunneri ICTs (2x315 MVA) | 400/220 kV Rachagunneri 3rd ICT 500 MVA & 4th ICT 500 MVA | It will relieve the overloading of existing ICTs Time line:March-2026 |
| 4 | 400/220 kV Vemagiri ICTs (3x315 + 1x500 MVA) | Expeditious commissioning of 400 kV Ainavalli S/S and its associated 220kV downstream (Timeline:Dec’25) | It will relieve the loading of Vemagiri ICTs Time line: June-2026 |
| 5 | 400/220 kV Gazuwaka ICTs (2x315 + 1x500 MVA) | Expeditious commissioning of 400/220kV Atchuthapuram s/s and its associated 220kV downstream system (Timeline: Jun’25) | It will relieve the loading of Gazuwaka ICTs and provide a reliable supply to the Vishakhapatnam area. Time line: December-2026 |

  - Vijayawada/ Vemagiri area Constraints

| Sl. No | Present Constraints | Action to be taken | Remarks |
| --- | --- | --- | --- |
| 1 | 220 kV Vemagiri-Duvva S/C | 400/220kV Gudivada charged in Feb’26 and associated 220kV lines needs to be commissioned . LILO of 220kV Gudivada - Bhimavaram/Akiveedu lines at 400kV Gudivada S/S. | It will relieve the 220kV line loadings in area. Time line: June-2026 |
| 2 | 220kV Vemagiri - Bommur three lines | 400/220kV Gudivada charged in Feb’26 and associated 220kV lines needs to be commissioned | Time line: June-2026 |
| 3 | 220kV Srisailam - Chalakurthy S/C |  | No update |
| 4 | 220kV Podili_400 - Podili_AP D/C | Replacement with HTLS | Time line: December-2026 |

  - Vishakhapatnam area Constraints

| Sl. No | Present Constraints | Action to be taken | Remarks |
| --- | --- | --- | --- |
| 1 | 220kV Kalpakka-Brandix D/C | Expeditious commissioning of 400/220kV Atchuthapuram S/S and its associated 220kV downstream system | It will relieve the loadings in down stream . Time line: December-2026 |
| 2 | 220kV Maradam-Bobbili D/C | Single LILO of 220kV Bobbili -Garividi DC line at 400/220kV Maradam S/S | Time line: December-2026 |
| 3 | 220kV Lower Sileru –Bommuru S/C | Expeditious commissioning of 220kV Lower Sileru - RC Varam | Forest department clearance awaited |

  - Rayalaseema area Constraints

| Sl. No | Present Constraints | Action to be taken | Remarks |
| --- | --- | --- | --- |
| 1 | 220kV Chinakampalli-Kadapa S/C | LILO of one circuit of 220kV Jammalamadugu - Poumamilla D/C at 220kV Mydukur | Time line: August-2026 |
| 2 | 220kV Rachaguneri - Renigunta D/C | Commissioning of 220Kv Avilala S/S , 220kV Avilala RachaguneriD/C line |  |
| 3 | 220kV Chittor-Thiruvallam S/c line is kept open due to overloading | Re-stringing of 220kV Chitoor- Thiruvallam S/C to HTLS |  |
| 4 | 220kV Chittoor- Chittoor_AP D/C |  |  |

    - Telangana

- Transmission Constraints with Relieving Measures with Anticipated Timeline

| Sl. No | Present Constraints | Action to be taken | Remarks |
| --- | --- | --- | --- |
| 1 | 400/220kV Ramagundam ICTs (2x315 + 2x250 + 1x200 MVA) | 400/220kV Nirmal ICT-4 and 220kv topology changes | It will relieve the overloading of existing ICTs |
| 2 | 400/220kV Dindi ICTs (2x315 MVA) | 400/220kV 315 MVA ICT-3 approved | Shifting of 1x315 MVA ICT to Dindi S/S approved as a temporary measure |
| 3 | 400/220kV Gajwel ICTs (2x315 + 2x500 MVA) | Load diversion to 400kV Narsapur |  |
| 4 | 400/220kV Damerchrla ICTs (2x500 MVA) | Additional ICT need to be planned | It will relieve the overloading of existing ICTs |
| 5 | 400/220kV Hyderabad ICTs (3x315+1x500 MVA) | 400/220kV 500 MVA ICT-5 approved in 39th CMETS | It will relieve the overloading of existing ICTs |
| 6 | 400/220kV Shankarpally ICTs (3x315+1x500 MVA) | Upgradation of 2x315 MVA ICT to 2x500 MVA ICT approved | Swapping of 1x315 MVA ICT at Shankarpally S/S with 1x500 MVA ICT at Bhupalapally approved as a temporary measure |
| 7 | 400/220kV Nirmal ICTs (3x315 MVA) | 400/220kV 315 MVA ICT-4 proposed | Shifting of 1x315 MVA ICT to Nirmal S/S approved as a temporary measure |

- Intra State Constraints

| S.No | Area | Constraints | Remedial Measure Given by State |
| --- | --- | --- | --- |
| 1 | North Telangana | 220kV Dichpally-Bheemgal S/C | Commissioning of 2nd circuit |
| 2 |  | 220kV Nirmal(400/220kV)-Nirmal_TS D/C | Commissioning of 3rd circuit |
| 3 |  | 220kV Rampur-Bheemgal S/C | HTLS re-conductoring will be done |
| 4 |  | 220kV Warangal-Nagaram D/C |  |
| 5 |  | 220kV Kalwakuntla-Thimmajipet D/C |  |
|  |  | 220kV Ramadugu-Durshed-D/C |  |
|  |  | 220KV Jangoan(400KV)-Jangoan-D/C |  |
|  |  | 220kV Oglapur-Huzurabad-S/C | TS informed augmentation will be planned |
| 6 |  | 220kV RSS - Durshed D/C |  |
| 7 | South Telangana | 220kV Suryapet-Miryalaguda D/C |  |
| 8 |  | 220kV Nagarjuna Sagar-Talapalli 1,2&3 | Re-Conductoring Kundah conductor with Moose Conductor |
|  |  | 220kV Shankarpally-Yeddumaularam-D/C |  |
|  |  | 220kV Dindi-Kalwakurthy-D/C |  |
|  |  | 220kV Veltoor-Wanaparthy-D/C |  |
| 11 |  | 220kVMahaboobnagr(400kV/220kV)-Mahaboobnagar_TS D/C |  |
|  |  | 220kV Ghanapur-Moulali S/C & 220kV Ghanapur-Infosys S/C |  |
| 12 |  | 220kV Bonglur - Chandrayngutta D/C |  |
| 13 | Over-Voltage | Over-Voltage at 32 Nos of S/S in Telangana. [ Asupaka, Chandulapur, Dindi, Gajwel, Ghanapur, Jangaon , Julurpadu, Kakatiya TPS, Kethireddypalli, Khammam, KTPS - VI, KTPS - VII, Maheswaram PG, Maheswaram TS, Malkaram, Mamidipalli , Medaram , Narsapur , Nirmal , Nizamabad, Ramadugu, Ramagundam , Shanakarpalli, Singareni, Srisailam LB, Sundilla, Suryapet, Tippapur, Tukkapur, Veltoor , Warangal | Expediting the commissioning already approved Bus-Reactors at Uddandapur (1x125 MVAr), Narlapur (1x125MVAr), Yedula 1x125MVAr), Vettam 1x125MVAr). In addition to above, TG to plan for additional reactive power compensation to mitigate the Over-Voltages. |

    - Karnataka

- Transmission Constraints – Relieving Measures with Anticipated Timeline – Short Term

| Sl. No | Action to be taken | Present Constraints | Remarks | Time line |
| --- | --- | --- | --- | --- |
| 1 | 400/220kV Kadandale SS | UPCL ICTs & 220kV UPCL-Kemar D/C line are severely over loaded. At present the Kemar bus split is operated thus resulting in many Disturbances in Mangalore area. | It will provide reliable supply to Mangalore area. Time line given was Dec-24. Yet to be commissioned | Feb-26 |
| 2 | 400/220kV Dommasandra SS | Hoody ICTs are critically loaded | Relieves Hoody ICTs. Time line given was Dec-24. Yet to be commissioned | Nov-25 |
| 3 | 400/220kV Peenya SS | Overloading of Nelamangala ICTs and 220kV Bangalore Network is highly loaded | Relieves Nelamangala ICTs | Mar-26 |
| 4 | 400/220kV Yalwar | Constraints in evacuation of RE generation in north Karnataka | Relieves Raichur (2x315+1x500) and Gulbarga (2x500) ICTs | Oct-26 |
| 5 | 400/220/110 kV Kustagi SS | Constraints in evacuation of RE generation in north Karnataka | Relieves Raichur (2x315+1x500) and Gulbarga (2x500) ICTs | Mar-26 |
| 6 | 400/220kV Kadakola SS | Mysore ICTs are critically loaded | Relives Mysore (2x315+2x500) ICTs | Dec-25 |
| 7 | 400/220kV Huliyurdurga SS | Nelamangala and Mysore ICTs are critically loaded | Relives Mysore (2x315+2x500) and Nelamangala (3x500) ICTs | Aug-26 |
| 8 | 400/220kV Guttur 3rd ICT 500 MVA | Evacuation of RE Generation in Davangere area | Relieves 400/220kV (3x315 MVA) | Approved in April 2024 meeting. Tentative 2027 |
| 9 | 400/220kV Mekhali S/S (2x500 MVA) | Evacuation of RE Generation and feeds loads in Narendra area | Relieves 400/220kV Narendra ICTs (2x500 MVA) | Approved in April 2024 meeting. Tentative March 2027 |

- Lines requiring Re- Conductoring

  - 400 kV & Inter-State

| Sl. No. | Constraint | Remedial action proposed by KPTCL vide letter date 22.05.2025 |
| --- | --- | --- |
| 1 | 400 kV Devanhalli – Hoody Twin Moose D/C to HTLS | TCCM approval communicated and survey of lines under process |
| 2 | 400 kV Yelahanka-Devanahalli S/C Twin Moose S/C to HTLS |  |
| 3 | 400kV Guttur - Hiriyur Twin Moose D/C |  |
| 4 | 220 kV Sedam – Tandur S/C |  |
| 5 | 400kV Pavagada - Gooty Twin Moose D/C | Reconductoring approved in 41st SR CMETS |

  - Existing 220 kV Transmission lines which are already planned for reconductoring (yet to be reconductored)

| Sl. No. | Constraint | Status & Timeline given by KPTCL vide letter dated., 22.05.2025 |
| --- | --- | --- |
| 1 | 220kV Nelamangala – Dabaspet S/C | Re-conductoring to HTLS by Dec 25 |
| 2 | Kali Complex re-conductoring to be expedited | Re-conductoring to HPC by Oct 25 |
| 3 | 220kV Shimoga – Bangalore 1,2,3&4 lines | Re-conductoring to HPC – LOI issued for survey (TCCM approved) |
| 4 | 220kV Mysore – Kadakola D/C | Re-conductoring to HPC – Mar 26 |
| 5 | 220kV Gadag – Doni D/C - This lines are kept open to avoid over-loading of 220kV Harti – Gadag during high wind season | Re-conductoring to HPC – Dec 25 |

- Bengaluru Constraints

| Sl. No | Present Constraints | Action to be taken | Status given by KPTCL vide letter dated 22.05.2025 |
| --- | --- | --- | --- |
| 1 | 400/220kV Bidadi ICTs 220kV Bidadi-Bidadi D/C 220kV Bidadi-Kumbalgod S/C 220kV Kumbalgod-Vrishabavathyvally S/C | Expedite Commissioning of the following: - 3rd ICT at Bidadi (POWERGRID) - 220kV Somanhalli – V Valley 2nd line - LILO of 220kV Bidadi – Somanahalli at 220kV V Valley | a. To be tendered. b. TCCM approval communicated and survey of lines under process. |
| 2 | 400kV/220kV Nelamangala (3X500 MVA) ICTs |  |  |
| 4 | 220kV Hoody-HAL D/C | The following lines are required to be commissioned - 220 kV Hoody – EDC - 220 kV Peenya to A -Station | a. Tendering stage b. Work under progress and expected date of commission: March 26 c. CEA suggested 400kV Transmission scheme to be revisited and accordingly, KPTCL is studying for alternative solution. |
| 5 | 220kV HAL-EDC S/C | The following lines are required to be commissioned - 220 kV Hoody – EDC - 220 kV Peenya to A -Station |  |
| 6 | 220kV Hoody- ITPL D/C | Need Additional interconnection with Dommasandra like - 220kV Sobha Dreams – Dommasandra S/C - 220kV EPIP – Dommasandra S/C | TCCM approval communicated and survey of lines under process. |
| 7 | 220kV HSR-Koramangala S/C | - Expedite Commissioning of - 220kV Hoody – EDC S/C UG Cable - 220kV EDC – Koramangala UG Cable - Requirement - 220kV HSR – Koramangala additional line | Same as Sl No-4,5 |
| 8 | 220kV Devanahalli- Hardware park D/C | The following lines are required immediately - 220kV KIADB – Gowribidanur (80% work completed) - 220kV Devanahalli-DB Pura 1&2 - 220kV Devanahalli – KIADB s/c | Mar 2026 |
| 9 | 220kV Hardware park- Begur D/C | The following lines are required immediately - 220kV KIADB – Gowribidanur (80% work completed) - 220kV Devanahalli-DB Pura 1&2 - 220kV Devanahalli – KIADB s/c - 220kV Devanahalli-Hoody S/C |  |
| 10 | 400/220kV Yelahanka ICTs 220kV Yelahanka-Yelahanka (DG) D/C 220kV Yelahanka-Sahakari Nagar D/C | Expedite Commissioning of the following: - 3rd ICT at Yelahanka (POWERGRID) - LILO of 220kV Manyatha/HRBR – ITI/Hoody lines at 400/220kV Devanahalli - Reconductoring of 220kV Yelahanka-Sahakari Nagar D/C is required - 220kV Yelahanka-Yelahanka (DG) D/C-3rd Cable is required | ICT-3 commissioning is expected by Mar 2026 |
| 11 | 220kV Tumkur (Madhugiri) –Antharasanahalli D/C | Reconductoring to be considered to utilize the - 400/220kV Tumkur 3x500 MVA - 220kV Tumkur – Antharsanahalli to HTLS (min 1400 Amps) - Will relieve Nelamangala ICT loading and Support towards Shimoga | Strengthening of 220kV Madhugiri – Antharasanahalli D/C. Timeline is not mentioned in the letter |
| 12 | 220kV Mylasandra-HSR D/C | Expedite the following: - Re-Conductor to HTLS - Plan 400/220kV Indiranagar or any 400/220kV SS near Hoody | a. Strengthening of existing 220kV Mylasandra- HSR Layout and Mylasandra-Naganathapura lines by HPC b. 400/220kV Indiranagar c. 400/220kV Yerandanahalli NEW |
| 13 | 220kV Mylasandra-Nagnathpura S/ | Expedite the following: - Re-Conductor to HTLS along-with 220kV Naganathpura – HSR S/C - Plan 400/220kV Indiranagar or any 400/220kV SS near Hoody |  |

- Kolar Constraints

| Sl. No. | Present Constraints | Action to be taken | Status given by KPTCL vide letter dated 22.05.2025 |
| --- | --- | --- | --- |
| 1 | 220kV Kolar (PG)-Kolar (KA) D/C | Expedite Commissioning of the following: - Re-conductoring to be expedited or 220kV Kolar (PG) - Malur - Commissioning of 400/220kV Dommasandra - 220kV Kolar-Kolar_KA D/C needs to be reconductored. | Strengthening of 220kV Kolar_PG – Kolar_KA D/C and 400kV/220kV Dommasandra / 400kV Doddathagahalli Work under progress and expected date of commission is Mar 2026 |

- Narendra Constraints

| Sl. No. | Present Constraints | Action to be taken |
| --- | --- | --- |
| 1 | 400kV /220kV Narendra ICTs | Expedite commissioning of the following: - 3rd ICT at 400/220kV Narendra S/S (POWERGRID). - 400/220kV Mekhali |
| 2 | 220kV Bidnal-Hubli D/C | Expedite Commissioning of 220kV Giriyal S/S |

- Narendra Constraints

| Sl. No | Present Constraints | Action to be taken | Status given by KPTCL vide letter dated 22.05.2025 |
| --- | --- | --- | --- |
| 1 | 400kV /220kV Narendra ICTs | Expedite commissioning of the following: - 3rd ICT at 400/220kV Narendra S/S (POWERGRID). - 400/220kV Mekhali | NA |
| 2 | 220kV Bidnal-Hubli D/C | Expedite Commissioning of 220kV Giriyal S/S | Estimation and DPR under preparation |

- Mysore Complex

| Sl. No. | Present Constraints | Action to be taken | Status given by KPTCL vide letter dated 22.05.2025 |
| --- | --- | --- | --- |
| 1 | 400/220kV Mysore ICTs | Even after commissioning of 4th ICT, Mysore ICTs loading is going beyond N-1 limits. Expedite Commissioning - 220kV Somanhalli – Harohalli Kanakpura – TK Halli – 2nd circuit to be expedited (SCOD – Sep 2017) - 400/220kV Kadakola S/S, Hampapura , Santhemaranhalli S/s | 400kV/220kV Kadakola and 400kV/220kV Hampapura Work in progress and NIT issued on 02.05.2025(TBCB) |
| 2 | 220kV Mysore – Kadakola D/C and 220kV Hootgally – Kadakola S/C | Expedite commissioning of 400/220kV Kadakola S/S | Sep-2025 |
| 3 | 220kV Hootgally – Vajamangala | 2nd circuit to be expedited | Work under Progress |
| 4 | 220kV Kadakola – Addakanhalli D/C | Expedite commissioning of 400/220kV Santhemaranhalli S/S | TCM approval communicated and survey of lines under process |

- Mangalore and Hassan Area Constraints

| Sl. No | Present Constraints | Action to be taken | Status given by KPTCL vide letter dated 22.05.2025 |
| --- | --- | --- | --- |
| 1 | 400kV /220kV UPCL ICTs | Expedite commissioning of the following: - 400/220kV Kadandale SS and downstream. - LILO of 220kV Kemar-MSEZ at Kadandale SS | Work under progress and expected to complete by Dec 2025 |
| 2 | 220kV UPCL-Kemar D/C (SPS implemented with 342 MW limit per circuit) |  |  |
| 3 | 220kV Hassan - CR_Patna S/C | Reconductoring to HPC | NA |
| 4 | 220kV Hassan_PG-Hassan_KA S/C | Reconductoring to HPC | NA |

- North Karnataka Constraints

| Sl. No | Present Constraints | Action to be taken | Status given by KPTCL vide letter dated 22.05.2025 |
| --- | --- | --- | --- |
| 1 | 400/220kV Kudgi NTPC ICTs 220kV Almatti – Bagalkot D/C 220kV Bagalkot – Vajramatti D/C | Expedite Commissioning of 400/220kV Yalwar S/S along-with the 220kV downstream system | Commissioning of 400kV Yelawar and 400kV Mekhali by Aug 2025 |
| 2 | 400kV/220kV Jindal (2X315 MVA) ICTs | Upgradation of 3rd ICT – 500 MVA | NA |
| 3 | During High Wind in North Karnataka - 400/220kV Raichur TPS ICTs - 400kV/220kV Kalaburgi (2 X 500 MVA) ICT - 220kV Gangavathy - Kusthagi S/C, - 220kV Kusthagi - Lingasugur S/C - 220kV Lingasugur - RTPS D/C - 220kV Lingasugur - Malat D/C - 220kV Sedam-Tandur S/C - 220kV Gangavathy-Kusthagi S/C | Expedite Commissioning of 400/220kV Kushtagi S/S Strengthening 220kV Lingasugur-Kushtagi-Gangavathy-Lingapura lines by replacing Drake with equivalent HPC Drake. | Dec 2025 |

- Hiriyur area Constraints

| Sl. No | Present Constraints | Action to be taken | Status given by KPTCL in letter dated 22.05.2025 |
| --- | --- | --- | --- |
| 1 | 400kV/220kV Guttur (2X315 MVA) ICTs | Augmentation of ICTs | New Constraint |
| 2 | 400kV/220kV Jagalur (2 X 500 MVA) ICTs | Augmentation of ICTs | New Constraint |
| 3 | 220kV Neelagunda-Guttur S/C | Reconductoring to HPC | New Constraint |
| 4 | 220kV Chitradurga-Hiriyur_PG S/C 220kV Tallak-Hiriyur_KA S/C 220kV Hiriyur_KA-Madhugiri S/C | Expedite Commissioning of - 220kV Chitradurga – Hiriyur (KA) S/C - 220kV Tallak – Hiriyur (PG) – 2nd line - 220kV Hiriyur – Madhugiri – 2nd line | Work under progress and expected to complete by March 2026 |

- Kali Complex Constraints

| Sl. No. | Constraints | Remedial Measure Given by State | Status given by KPTCL in letter dated 22.05.2025 |
| --- | --- | --- | --- |
| 1 | 400kV/220kV Talaguppa (3 X 315 MVA) ICTs | NA | NA |
| 2 | 220kV Sharavathy-MRS_Shimoga 1,2&3 | Reconductoring to HTLS is approved | Works are not yet started |
| 3 | 220kV Nagjheri – Ambewadi DC | Strengthening the 220 kV lines emanating from Nagjhari generating station towards Ambewadi by replacing Drake conductor by Drake equivalent HTLS conductor. | Estimate and DPR under preparation |
| 4 | 220kV Ambewadi – Narendra DC |  |  |
| 5 | 220kV Kodasalli – Nagjheri D/C |  |  |
| 6 | 220kV Kaiga – Kodasally SC |  |  |
| 7 | 220kV Kaiga-Kadra SC |  |  |
| 8 | 220kV Naghjeri-Hubli1,2 & 3 and Nagjheri-Bidnal |  |  |
| 9 | 220kV Kadra – Kodasally SC |  |  |
| 10 | 220kV Bidnal-Hubli D/C |  |  |

    - Kerala

- Transmission Constraints – Relieving Measures with Anticipated Timeline

  - ISTS Constraints

| S. No. | Constraints | Remedial Measure Given by State |
| --- | --- | --- |
| 1 | 400/220 kV 2X315 +1X500 MVA ICTs at Kozhikode SS | 400/220 kV Kasargode S/S , 400/220kV Wayanad S/S |
| 2 | 400/220 kV 2X315 MVA ICTs at Thrissur HVDC SS | Commissioning of ICT 3 |

  - Intra State Constraints

| S. No | Constraints | Remedial Measure Given by State |
| --- | --- | --- |
| 1 | 220kV Areakode-Kanhirode S/C | Commissioning of 400kV Udupi - Kasargode - Wayanad |
|  | 220kV Areacode- Orkkattery S/C |  |
|  | 220kV Areakode – Kunnamangalam S/C |  |

- Tamil Nadu

- Transmission Constraints – Relieving Measures with Anticipated Timeline – Short Term

| Sl. No | Present Constraints | Action to be taken | Remarks | Timeline |
| --- | --- | --- | --- | --- |
| 1 | Kalivanthapattu ICTs & 230kV downstream lines are severely over loaded. | Commissioning of 400/230kV Tharamani S/S, 400/230kV Guindy S/S & 400/230kV Kalivanthapattu ICT-4 (500 MVA) | It will provide reliable supply to South Chennai area. | Mar-24 (Not commissioned) |
| 2 | Alamathy ICTs & 230kV downstream lines are severely over loaded. | Commissioning of 400/230kV Korattur S/S & 400 kV Thervoykandigai S/S along with associated lines | It will provide reliable supply to North Chennai area. | Mar-24 (Not commissioned) |
| 3 | Arasur ICTs & 230kV downstream lines are severely over loaded. | Commissioning of 400/230kV Edayarpalayam S/S along with associated lines | It will provide reliable supply to Coimbatore area. | Mar-24 (Not commissioned) |
| 4 | NLC TS2 ICTs, NNTPP ICTs & 230kV downstream lines are severely over loaded. | Commissioning of 400/230kV NLC TS2 ICT-3 (315 MVA), 400/230kV Ariyalur S/S, 400/230kV Manalmedu S/S & 400/230kV Cuddalore S/S along with associated lines | It will provide reliable supply to Neyveli area. | Mar-22 (Not commissioned) |
| 5 | Salem ICTs & 230kV downstream lines are severely over loaded. | Commissioning of 400/230kV Mangalapuram S/S along with associated lines | It will provide reliable supply to Salem area. | Jul-23 (Not commissioned) |
| 6 | Trichy ICTs & 230kV downstream lines are severely over loaded | Commissioning of 400/230kV Thuraiyur S/S along with associated lines | It will provide reliable supply to Trichy area. | Mar-22 (Not commissioned) |
| 7 | Udumalpet ICTs & 230kV System | 230kV Mywadi-Kurukathy LILO at 400/230kV Rasipalyam 230kV Kurukathy-Palladam LILO at 400/230kV Rasipalyam Commissioning of 400/230kV Edayarpalayam S/S along with associated lines | It will provide reliable supply to Coimbatore area | Mar-24 (Not commissioned) |

- Chennai area constraints

| S. No. | Present Constraints | Actions to be taken |
| --- | --- | --- |
| 1 | 400kV Thiruvallam-Kalivanthapattu D/C | Expeditious commissioning of 400kV/230kV Taramani S/S, 400kV/230kV Guindy S/S |
| 2 | 230kV Kalvindapattu-Veerapuram S/C |  |
| 3 | 230kV Kalivindapattu-Taramani S/C |  |
| 4 | 230kV Almathy-Thiruverukadu S/C | Expeditious commissioning of 400kV NCPS – Manali S/C line,400kV/230kV Korattur S/S, 400kV/230kV Thervoykandigai S/S & 230kV Avadi S/S |
| 5 | 230kV Manali-CMRL S/C | Expeditious commissioning of 400kV Guindy S/S & commissioning of 230kV CMRL Central – Mambalam UG Cable |
| 6 | 230kV Manali – Korattur S/C line |  |
| 7 | 230kV Guindy – Porur S/C line | Expeditious commissioning of 400kV/230kV Guindy S/S |
| 8 | 230kV Guindy – Alandur_CMRL S/C line |  |
| 9 | 230kV SV Chatram-Oragadam D/C | Expeditious commissioning of 230kV Maraimalai Nagar S/S |
| 10 | 230kV Taramani – R A Puram S/C line | Expeditious commissioning of 400/230kV Taramani SS and 400/230kV Guindy S/S |
| 11 | 230kV Taramani – Kitz S/C line |  |
| 12 | 230kV Taramani – Mylapore S/C line |  |
| 13 | 230kV Kanchipuram – Arni S/C | Commissioning of generation at Bhavini |

- Hosur Area constraints

| S. No. | Present Constraints | Actions to be taken |
| --- | --- | --- |
| 1 | 230kV Hosur (PG) - Hosur (TN) D/C | Expeditious commissioning of 400/230-110 kV Ulagam S/S |
| 2 | 230 kV Hosur (PG)– Gurubrapalli S/c |  |
| 3 | 230kV Hosur (PG) –Thirupattur S/c |  |

- Neyveli Area constraints

| S. No. | Present Constraints | Actions to be taken |
| --- | --- | --- |
| 1 | 230kV NNTPP-Neyveli (TN) D/C | Expeditious commissioning of 400/230kV Ariyalur S/S, 400/230kV Manalmedu S/S & 400/230kV Cuddalore S/S along with associated lines |
| 2 | 230kV Neyveli TS2-Kadalangudy S/C |  |
| 3 | 230kV Neyveli (TN)-Kadalangudy S/C |  |
| 4 | 230kV Cuddalore-Villupuram S/C |  |
| 5 | 230kV Neyveli TN-Shankarapuram S/C |  |
| 6 | 230kV STCMS-Cuddalore S/C |  |

- Coimbatore Area

| S. No. | Present Constraints | Actions to be taken |
| --- | --- | --- |
| 1 | 230 kV Arasur – Arasur (PG) D/C | Expeditious commissioning of the following transmission system - 400/230-110kV Edayarpalayam S/S. - 230/110kV Kalivelampatty S/S (LILO of 230kV Arasur (PG) - Ingur SC line) - LILO of 230kV Karuvalur – Shenbagapudur S/c at 400/230kV Arasur (PG) S/S |
| 2 | 230 kV Arasur – Karavalur S/C |  |
| 3 | 230kV Arasur-Thirupur S/C |  |
| 4 | 230kV Udumalpet-Mywadi D/C | Expeditious commissioning of 400/230-110kV Edayarpalayam S/S |
| 5 | 230kV Coimbatore- Othakalmandapam S/C |  |
| 6 | 230kV Othakalmandapam-Tudiyalur S/C |  |
| 7 | 230 kV Othakalmandapam – Mywadi S/C |  |
| 8 | 230kV Palladam-Sadayapalayam S/C | Expeditious commissioning of the following: - LILO of 230kV Kurkathi – Mywadi S/c line and 230kV Kurkathi – Palladam S/c line at 400/230-110kV Rasipalayam S/S |

- Tuticorin, Madurai, Trichy & Pugalur Area constraints

| S. No. | Present Constraints | Actions to be taken |
| --- | --- | --- |
| 1 | 230 kV Trichy (PG) – Allundur (TN) D/C | Additional 230kV link lines from Alundur 230kV SS to Trichy 230KV SS and Thatchankurichi 230 KV is under proposal and consideration. |
| 2 | 230 kV Pugalur – Pugalur (PG) D/C | Expeditious commissioning of 230kV Pugalur PG - Nallur S/S and 230kV Nallur S/S |
| 3 | 230 kV Pugalur-Karukathi S/C | Expeditious commissioning of the following: - 400/230-110 kV Edayarpalayam S/S. - LILO of 230kV Kurkathi – Mywadi S/c line and 230 kV Kurkathi – Palladam S/c line at 400/230-110 kV Rasipalayam S/S. |
| 4 | 230 kV Pugalur- Pudanchandai S/C |  |
| 5 | 230 kV Pugalur- Valayapatti S/C |  |
| 6 | 230kV Karaikudi – Pudukottai S/C | Expeditious commissioning of the following: - 230kV K.Pudur S/S - 230 kV Muthuramalingapuram- K.Pudur line |
| 7 | 230kV Karaikudi_PG - Karaikudi_TN D/C | Reconductoring of the line to HTLS |
| 8 | 230kV Madurai (TN)-Samayanallur S/C | Reconductoring of the line to HTLS or 230kV Madurai (TN)-Samayanallur 2nd ckt |
| 9 | 230kV Samavanallur-Alagarkovil S/C | Reconductoring of the line to HTLS or 230kV Samavanallur-Alagarkovil 2nd ckt |
| 10 | 230kV Madurai-Sembatty S/C | Expeditious commissioning of 230kV Madurai –Sembatty second circuit. |
| 11 | 230kV KKNPP-TTPS S/C | Expeditious commissioning of 400/230 kV Samugarengapuram S/S |
| 12 | 230kV Udayathoor - Tirunelveli S/C |  |

- Puducherry

- ISTS Constraints

  - 400kV NNTPP – Puducherry: Tripping will lead to low voltage in 230kV Puducherry network

  - 230kV Neyvelli–Villianur S/C is overloaded